SynerGEE Gas software developed by Stoner Associates, Inc of Carlisle, PA, is used in the hydraulic design calculations of our present and proposed pipeline facilities.  This proprietary program uses various equations and subroutines to calculate the pipeline pressures and flows.  A description of the major basic equations and associated variables and assumptions are presented below:

# Flow Equation: (FM – Fundamental Equation with Flow Dependent Friction)

Q = 77.54 (Tb/Pb) (D^2.5) E  { (P1^2 – P2^2 – (0.0375G(h2-h1)Pa^2 )/ Z Ta) / G Ta L Z f }^0.5

where:

Q 	= Flowrate, Standard Cubic Feet per day

Tb	= Gas Base Temperature; 520 degree Rankine

Pb	= Gas Base Pressure; 14.73 pounds per square inch absolute (psia)

D	= Pipeline Internal Diameter, inches

L	= Pipeline Length, miles

E 	= Pipeline Efficiency; 1.0, dimensionless

P1	= Upstream Node Pressure (psia)

P2	= Downstream Node Pressure (psia)

G 	= Specific Gravity of the Gas in the Pipe; 0.585, dimensionless

h2 	= Upstream Node Elevation ft (elevation effects not used)

h1 	= Downstream Node Elevation ft (elevation effects not used)

Pa 	= Average Pipeline Pressure (psia)

Ta 	= Average Gas Flowing Temperature for a Pipe, degree R

Z 	= Gas Compressibility Factor, dimensionless

f 	= Pipeline Darcy-Weisbach Friction Factor, dimensionless

1 / f^0.5  =  -2 log { ( e / d / 3.7) + (2.51 / Re (f^0.5) }

e 	= Absolute Roughness of Pipes, 1,800 micro-inches

d 	= Pipe Internal Diameter

e/d 	= Relative Roughness

Re	= Reynolds Number, dimensionless

Texas Gas uses design temperatures obtained from historic gas flowing parameters and from thermal model (Stoner’s SynerGee) results using published atmospheric ambient temperatures from the U. S. Department of Commerce Publications, further correlated to various soil temperatures at specified pipe depths, seasons, and general geographic locations.  Pipeline efficiencies and absolute roughness values are derived from actual operating or test data for the system.

The brake horsepower requirements at the compressor stations are calculated by the use of standard curves supplied by the compressor manufacturers that have been modified to reflect Texas Gas’ experience.

The daily design capacity is predicated upon Texas Gas’ ability to meet each firm customer’s maximum contract quantity (Contract Demand) on the same day.  In cases where a customer has multiple delivery points (conjunctive billing), the maximum daily contractual obligation to the customer is prorated to each of the various delivery points based on historic utilization of those points.  The market areas on the Texas Gas system, which are subject to variation in demand as a result of temperature fluctuations, lie in the NE-SW direction and consist of the Memphis-Evansville-Louisville-Indianapolis geographical areas.  Most of the cold fronts approach this area from the northwest.  As a result, these market areas generally experience their peak demands on the same day.

All material specifications, design, construction, and testing of facilities are in accordance with Minimum Federal Safety Standards for Transportation of Natural Gas by Pipeline, Part 192, Title 49, Code of Federal Regulations.