## O(3) App A
Docket No. RP06-
Statement O(3)
Appendix A
Page 1 of 3
NORTHWEST PIPELINE CORPORATION
FLOW DIAGRAM ASSUMPTIONS AND FORMULAE
Basic Assumptions - The following assumptions were made in developing the design and flow
diagrams of Exhibit G/G-I:
1) | Gas Properties:
Pb | = | Standard Pressure Base |  |  | 14.73 | psia
Tb | = | Standard Temperature Base |  |  | 60 | °F
G | = | Typical Specific Gravity |  |  | 0.6 | (dimensionless)
HHV | = | Higher Heating Value |  |  | 1000 | BTU/SCFT
k | = | Ratio of Specific Heats |  |  | 1.3 | (dimensionless)
m | = | Absolute (Dynamic) Viscosity |  |  | 2.5 x 10-7 | lbf-sec/ft2
Z | = | Compressibility - a modified Benedict-Webb-Rubin equation based on
the reduced pressure and temperature of the gas is used to approximate
the Standing-Katz correlation for Z (Trans AIME, Vol. 146, p. 144,942).
| Note: | The delivery volumes are converted from the thermal contractual
quantities (Dth/d) to volumetric quantities (MSCFD), using a one-to-one conversion
factor. Since the average heating value of gas received may exceed 1000 BTU/SCFD,
this conservative assumption effectively provides a small operational diversity factor to
help accommodate small imbalances and deviations from the uniform hourly flows.
Assumed Gas and Air Temperatures
| Tf = Mainline Flowing Temperature |  |  | 60.0 Deg F
| Ts = Mainline Suction Temperature |  |  | 60.0 Deg F
| Ta = mainline Ambient Temperature |  |  | 80.0 Deg F
| Tf = Lateral Flowing Temperature |  |  | 40.0 Deg F
| Ts = Lateral Suction Temperature |  |  | 40.0 Deg F
| Ta = Lateral Ambient Temperature |  |  | 40.0 Deg F
2) | Elevations and distances are determined from U.S.G.S. quadrangle maps and
construction records.
3) | Engine fuel consumption rates and power derate factors for elevation, ambient
temperatures, peripheral and auxiliary losses are in accordance with manufacturer’s
recommendations, industry standards and engineering records.
Docket No. RP06-
Statement O(3)
Appendix A
Page 2 of 3
NORTHWEST PIPELINE CORPORATION
FLOW DIAGRAM ASSUMPTIONS AND FORMULAE
Calculation Procedures - The following solution procedures were used in developing the design and
flow diagrams.
All hydraulic design and hydraulic system capacity calculations were performed using the steady-state
version of SynerGEE Gas, Version 4.xx, as marketed by Stoner Associates, Inc. of Mechanicsburg, PA.
Pipeline Design - The following formulae outline the major equations associated with pipeline gas flow:
Pipeline Flow Equation - The equation used for pressure loss through a pipe is referred to as the
“fundamental equation with flow dependent friction”. It takes the form:
Where:
| Q | = | Flow Rate |  | (scf/d)
| Tb | = | Temperature Base |  | (°R)
| Pb | = | Pressure Base |  | (psia)
| D | = | Pipe Inside Diameter |  | (in.)
| P1 | = | Upstream Pressure |  | (psia)
| P2 | = | Downstream Pressure |  | (psia)
| Tf | = | Flowing Gas Temperature |  | (°R)
| L | = | Pipe Length |  | (miles)
| Pa | = | Average Pressure |  | (psia)
| f | = | Friction Factor |  | (dimensionless)
| H1 | = | Upstream Elevation |  | (feet)
| H2 | = | Downstream Elevation |  | (feet)
| Z | = | Compressibility at Pa |  | (dimensionless)
Docket No. RP06-
Statement O(3)
Appendix A
Page 3 of 3
NORTHWEST PIPELINE CORPORATION
FLOW DIAGRAM ASSUMPTIONS AND FORMULAE
Friction Factor Equation - The equation used for determining the pipeline friction factor known as
the Colebrook-White equation takes the form:
Where:
| e | = | Effective Surface Roughness |  | (in.)
| d | = | Inside Pipe Diameter |  | (in.)
| Re | = | Reynolds Number |  | (dimensionless)