Northern Border Pipeline Company

Terminal Value Study

August 2005

Introduction

Northern Border Pipeline Company (NBPL) owns an interstate natural gas pipeline system that originates at the Montana/Canadian Border at Port of Morgan, Montana and runs southeasterly through Montana, North Dakota, South Dakota, Minnesota, Iowa, Illinois and Indiana to its terminus in North Hayden, Indiana.  NBPL’s major assets include approximately 1,395 miles of large diameter pipeline, 16 compressor stations with a total of 499,000 horsepower of installed compression, eight receipt stations and 48 delivery stations.

This study outlines the requirements and costs associated with the abandonment of all Northern Border Pipeline facilities pursuant to the regulations defined in DOT 192.727.

Description of Facilities

Pipeline System

NBPL’s pipeline system consists of approximately 822 miles of 42 inch diameter pipeline, 371 miles of 36 inch diameter pipeline and 202 miles of 30 inch diameter pipeline. In addition, the system contains 92 valve settings.

Schedule 1 provides an overview of NBPL’s pipeline facilities.

Compression

NBPL currently owns 16 compressor stations with a total of 499,000 horsepower of installed compression in six states.  In April 2006, Northern Border will commission an additional compressor station in Iowa, bringing the system total to 17.

In addition to a single compressor and driver (gas turbine or electric motor), each station includes an inlet and discharge piping system, a mainline valve setting with a launcher and receiver, a metered fuel (gas or electric) system, an air system that includes compression, a standby electric generation system, various monitoring, control, safety and communication systems as well as various buildings, roads, fences and other facilities used for the operation and maintenance of the station.  In addition, 12 of the 17 stations are equipped with a gas cooling system.

Schedule 2 provides a plot plan of a typical compressor station layout.

Meter Stations

NBPL owns 48 delivery stations and eight receipt stations throughout its system.  These stations vary in size from those that normally flow less than 500 MCF/day to those that flow over 500,000 MCF/day.  NBPL’s meter facilities generally fall into one of two categories.  The first is facilities that, on average, flow greater than 100,000 MCF/day.  These facilities are generally receipt or delivery interconnects with other pipelines.  The second group is those facilities that flow less than 100,000 MCF/day.  These facilities generally serve end-use customers such as industrial facilities or local distribution companies.

Schedule 3 shows the layout of a typical measurement station serving an end-use customer.

Estimating Methodology

The cost estimates for the abandonment of all pipeline, compressor station and metering facilities are based on the following assumptions:

- NBPL would file a FERC Section 7 application to abandon all of its facilities.  This application would include all required environmental studies and reports.

- All above grade facilities at mainline valve settings, compressor station and meter stations would be removed.  All below grade facilities at compressor and meter stations will be removed to a depth of at least two feet below the surface.  Any ground disturbance would be restored to the condition of the surrounding area.  Salvageable metal would be sold.  All other materials would be disposed of in an environmentally appropriate manner.

- Except as described below, all below grade line pipe would be removed, cut, hauled to the nearest compressor station and then sold for the value of the scrap steel.  Any ground disturbance would be restored to substantially its previous condition.

- All road, rail and major water body crossings would be capped, filled with concrete and abandoned in place.

- Contractors would be required to comply with all applicable environmental and safety regulation and would be responsible for the appropriate disposal of all non-salvageable material.

- All abandonment costs are based on consultations with contractors who have built NBPL facilities and have experience with abandonment projects.

- Inspectors would be present throughout the abandonment process to ensure all environmental and safety requirements are met.

- All salvage scrap metal material has been valued at $94.80/ton.

- All right-of-way easements would revert back to the landowner and all property owned in fee would be sold for its currently assessed valuation.

- All costs are in constant 2005 dollars

- All estimates assume that all demolition work can proceed in a continuous manner so as to take advantage of the economy of scale that such a large project offers.

Abandonment of Pipeline Facilities

The abandonment of NBPL’s large, 30 to 42 inch diameter lines would require that the pipeline be removed at the end of its useful life.  While the removal of other, smaller diameter pipelines may not be necessary, abandoning NBPL’s larger diameter lines in place would continue to subject the company to considerable safety and environmental risk as a result of the possibility that these lines would eventually corrode and collapse, creating trenches in the existing topography that would be dangerous to farmers and change the course of natural drainage.  As a result, these large diameter lines would generally need to be removed once they are taken out of service.  In this case, the line pipe that is removed would be sold and the salvage value would offset a portion of the removal cost.

In areas where it is not economically or environmentally practical to remove the pipeline, the segment of pipe would be cut, capped and filled with concrete in order to prevent any future collapse of the line.  For purposes of this study, all road, rail and major water body crossings have been assumed to be abandoned in place.

The estimate for the abandonment of pipeline facilities is based on input provided by pipeline contractors and salvage vendors.  Estimates are based on the contractor meeting all requirements of the FERC Plan and Procedures and assume that the pipe taken up would be cut and transported to the nearest compressor station location for final disposition by a salvage vendor.  The estimate does not include any cost for any unusual remediation or drain tile repair.

The value for salvage steel used in the study is based on the average scrap steel price from 2000 through 2004 as published by the United States Geological Service.  This average value of $94.80 per short ton is higher than the values quoted by several scrap vendors that were contacted.

Finally, the total pipeline removal cost is net of the value for recoverable line pack.  Based on input from a vendor that specializes in providing temporary compression for the recovery of line pack, approximately 92.4% of Northern Border’s line pack can be economically recovered.  The net credit to the total removal cost for recovering this pack is $24.6 million.

Details of the net pipeline abandonment costs are presented in Schedule 4.

Abandonment of Compression Facilities

As outlined in the assumptions above, NBPL’s 17 compressor stations would be removed and the land on which they currently stand would revert to its former use.  All foundations would be removed to at least two feet below grade.  All other materials would be removed in their entirety and either sold for salvage or disposed of in an appropriate manner.

All material is assumed to be salvaged for the scrap metal value.  The vast majority of equipment that is installed in the natural gas transmission industry is new.  This equipment is designed to meet specific flow, pressure and gas composition envelops.  In addition, the cost to refurbish used equipment often approaches the cost of new equipment.  As a result, to assume any salvage value greater than the value of the underlying raw material is inappropriate.

Removal estimates are based on input from contractors who have both built NBPL compression facilities as well as removed other compressor station facilities.  Estimates are based on the removal of NBPL’s CS11, which is typical of NBPL’s stations.  Costs are net of salvage and include the appropriate disposal of all non-salvageable material.  Estimates do not include any cost for any unusual environmental remediation.

Details of the compressor station abandonment costs are presented in Schedule 5.

Abandonment of Measurement Facilities

Meter station abandonment costs are based on information provided by industry contractors for the removal of a typical NBPL delivery station.  While the size and complexity of meter stations vary, the use of applying typical costs is appropriate since inspection costs, contractor mobilization and disposal of materials does not vary significantly among stations.

The majority of equipment and material would have only scrap value due to obsolescence, the duration equipment has been used, as well as the lack of a significant market for used equipment.

Total Abandonment Costs

Schedule 6 consolidates all of the above referenced costs and represents the total retirement costs for NBPL’s transmission system.  As is consistent with large projects that Northern Border builds, the total cost includes a 10% contingency to cover unidentified or difficult-to-quantify items that would manifest themselves in a project of this size.