## Summary Sheet
Exhibit No. DCP-27
Page 3 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
Summary All Facilities
Estimated
Cost
(March 2006$)
I. | Project Management
| A. | Pre-abandonment | [5 empty] | 540000
| B. | Abandonment | [5 empty] | 1780000
|  |  |  | Percentage of II, IV, V = | 6.34% |  | Total I. | 2320000
II. | Contract Expense
| A. | Engineering | [5 empty] | 260000
| B. | Environmental | [5 empty] | 1204600
|  |  |  | Percentage of IV, V = | 4.169% |  | Total II. | 1464600
III. | Property Tax | [6 empty] | 4230324
[7 empty] | Total III. | 4230324
IV. | Onshore Demolition Work
| A. | Equipment removal from buildings | [5 empty] | 60775
| B. | Outdoor equipment removal | [5 empty] | 844337
| C. | Dismantle rigid frame buildings | [5 empty] | 333498.39
| D. | Purge, clean and dismantle LNG storage tanks | [5 empty] | 16723236.9551
| E. | Asbestos siding removal and disposal | [5 empty] | 560328.3
| F. | Demolish masonary buildings | [5 empty] | 146828.58
| G. | Disposal costs | [5 empty] | 37650
| H. | Pipe removal | [5 empty] | 346663.5
| I. | Site work | [5 empty] | 2004030
| J. | Removal of misc. steel structures | [5 empty] | 26014
| K. | Cap TL-522 | [5 empty] | 15000
| L. | Power cable removal | [5 empty] | 9390
[7 empty] | Total IV. | 21107751.7251
V. | Offshore Demolition Work
| A. | Phase 1
|  | 1 | Removal of equipment |  |  |  |  | 932391.7733
|  | 2 | Removal of pipe |  |  |  |  | 312778.656
|  | 3 | Removal of electrical cable |  |  |  |  | 2885.76
|  | 4 | Disposal of material and equipment |  |  |  |  | 238543.04
[7 empty] | Subtotal: | 1486599.2293
Exhibit No. DCP-27
Page 4 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
Summary All Facilities
Estimated
Cost
(March 2006$)
V. | Offshore Demolition Work (continued)
| B. | Phase 2
|  | 1 | Removal of pipe trestle, roadway panel, and roadway beam |  |  |  |  | 1524400
|  | 2 | Breakup of deck platforms |  |  |  |  | 423302.4
|  | 3 | Removal and disposal of deck platforms |  |  |  |  | 2719200
|  | 4 | Removal of walkways |  |  |  |  | 432600
|  | 5 | Removal of mooring dolphin caps |  |  |  |  | 679800
[7 empty] | Subtotal: | 5779302.4
| C. | Phase 3
|  | 1 | Pile cap cutting |  |  |  |  | 460000
|  | 2 | Pile cutting |  |  |  |  | 671200
|  | 3 | Tunnel access shaft removal |  |  |  |  | 787200
|  | 4 | Pile removal |  |  |  |  | 4395525
|  | 5 | Bottom debris check and clearance |  |  |  |  | 439000
[7 empty] | Subtotal: | 6752925
[7 empty] | Total V. | 14018826.6293
VI. | Salvage
| A. | Equipment | [5 empty] | -787351
| B. | Valves | [5 empty] | -23200
| C. | Material
|  | 1 | Aluminum |  |  |  |  | -2656800
|  | 2 | Carbon steel plate |  |  |  |  | -1074249.3156
|  | 3 | Carbon steel pipe |  |  |  |  | -79800
|  | 4 | Stainless steel pipe |  |  |  |  | -950400
|  | 5 | Stainless steel plate |  |  |  |  | -3045693.1557
|  | 6 | Structural steel |  |  |  |  | -56568
|  | 7 | Electrical cable |  |  |  |  | -123000
[7 empty] | Total VI. | -8797061.4713
VII. | Contingency |  |  | (10% of I, II, IV, V) |  |  |  | 3891117.8354
[6 empty] | Grand Total: |  | 38235558.7186

## Project Management
Exhibit No. DCP-27
Page 5 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
I. Project Management
It is estimated that Cove Point will begin planning to retire its LNG plant two years prior to commencement of retirement
activities. Further it is estimated that the retirement project will take one year. Costs have been included in the estimate to
provide an allowance for company personnel used to assist the general contractor and subcontractors with dismantling
the plant and helping to assure project safety and security.
| A. Pre-Abandonment |  |  | Unit | No. | Days | Rate | Total
|  | 1 | Project management | person | 1 | 260 | 800 | 208000
|  | 2 | Environmental | person | 1 | 260 | 800 | 208000
|  | 3 | Office support | person | 1 | 260 | 400 | 104000
|  | 4 | FERC 7(b) abandonment application | person | 1 | 10 | 800 | 8000
|  | 5 | Land / ROW (legal) | person | 1 | 10 | 1200 | 12000
540000
B. Abandonment
|  | 1 | Project management | person | 2 | 260 | 800 | 416000
|  | 2 | Environmental coordinator (office) | person | 1 | 260 | 800 | 208000
|  | 3 | Office support | person | 1 | 260 | 400 | 104000
|  | 4 | LNG plant personnel | person | 10 | 130 | 800 | 1040000
|  | 5 | Land / ROW (legal) | person | 1 | 10 | 1200 | 12000
1780000
[5 empty] | Total project management: |  |  | 2320000

## Contract Expense
Exhibit No. DCP-27
Page 6 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
II. Contract Expense
| A. Engineering |  |  |  |  | Unit | No. | Days | Rate | Total
|  | 1 | Inspection of LNG plant |  |  | person | 2 | 15 | 800 | 24000
|  | 2 | Plans, specifications and estimate |  |  | person | 2 | 60 | 800 | 96000
|  | 3 | Prepare bid documents and attend meetings |  |  | person | 2 | 75 | 800 | 120000
|  | 4 | Travel expenses |  |  | trip | 10 |  | 1500 | 15000
|  | 5 | Misc. office expense |  |  | L.S. |  |  |  | 5000
[5 empty] | Total engineering expense: |  |  |  |  | 260000
B. Environmental
|  | 1 | Environmental assessment of LNG plant
|  |  | a. | Inspection and assessment of LNG facilities |  | person | 2 | 15 | 800 | 24000
|  |  | b. | Create sampling plan |  | person | 2 | 15 | 800 | 24000
|  |  | c. | Lab analysis of pre-abandonment samples |  | each | 50 | 30 | 150 | 225000
|  |  | d. | Evaluation and reports |  | person | 2 | 15 | 800 | 24000
[9 empty] | Subtotal: | 297000
|  | 2 | Environmental monitoring during abandonment
|  |  | a. | Environmental consultant (on-site) |  | person | 2 | 260 | 800 | 416000
|  |  | c. | Lab analysis of abandonment field samples |  | each | 50 | 60 | 150 | 450000
|  |  | d. | Evaluation and reports |  | person | 1 | 52 | 800 | 41600
[9 empty] | Subtotal: | 907600
[5 empty] | Total environmental expense: |  |  |  |  | 1204600

## Property Tax
Exhibit No. DCP-27
Page 7 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
III. Property Tax
It is estimated that it will take one year to demolish the terminal and restore the premises to a natural setting.
Cove Point must pay property tax for this one-year period and until title to the property is transferred to third party.
Property Tax
Paid in
[5 empty] | State | County | Yr. 2005
[5 empty] | Maryland | Calvert | 4230324
|  |  |  | Total property tax: |  |  | 4230324
Property Tax Breakdown for 2002, 2003, and 2004 Vintages
[6 empty] | Percent of | Property Tax
[5 empty] | Original | Plant | Paid in
[5 empty] | Cost | In-Service | Yr. 2005
|  | Plant in service 12/31/05 |  |  | 262748165 | 100% | 4230324
Pro-Rated
[6 empty] | Percent of | Property Tax
[5 empty] | Original | Plant | Paid in
|  | Vintage | Facility |  | Cost | In-Service | Yr. 2005
|  | 2004 | Tank E |  | 41460408 | 15.78% | 667524.9626
|  |  | Total 2004 Vintage: |  | 41460408 |  | 667524.9626
|  | 2003 | ASU |  | 15426681 | 5.871% | 248374.1756
|  | 2003 | M&R |  | 1911194 | 0.7274% | 30770.7947
|  |  | Total 2003 Vintage: |  | 17337875 |  | 279144.9703
|  | 2002 | Liquefaction |  | 21909701 | 8.339% | 352752.7356
|  |  | Remainder |  | 182040181 | 69.28% | 2930901.3315
|  |  | Total 2002 Vintage: |  | 203949882 |  | 3283654.0671

## Onshore Dem 1
Exhibit No. DCP-27
Page 8 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
IV. | Onshore Demolition Work | [7 empty] | Estimated
Cost
[6 empty] | Unit | No. | Unit Cost | (2006$)
A. Equipment removal from buildings
1. Booster pump building (103-H)
|  | a. | Send out booster pumps (1300 HP) |  | (10 pumps) | each | 10 | 250 | 2500
2. LNG vaporizer building (104-H)
|  | a. | Misc equipment |  | (10 items) | each | 10 | 1750 | 17500
3. Generator building (105-H)
|  | a. | Gas turbine generators (8.4 KW) |  | (3 turbines) | each | 3 | 2500 | 7500
4. LNG compressor building (106-H)
|  | a. | LNG booster pump (400 HP) |  | (3 pumps) | each | 3 | 250 | 750
|  | b. | Vapor compressor (400 HP) |  | (1 compressor) | each | 1 | 250 | 250
5. Boil-off compressor building (107-H)
|  | a. | Boil-off vapor compressors (1500 HP) |  | (3 compressors) | each | 3 | 10500 | 31500
|  | b. | Air compressor 125 HP skid mounted |  | (1 compressor) | each | 1 | 175 | 175
6. Fire pump building (110-H)
|  | a. | Fire pumps (300 HP) |  | (2 pumps) | each | 2 | 250 | 500
|  | b. | Jockey pump (10 HP) |  | (1 pump) | each | 1 | 100 | 100
|  |  |  | Total equipment removal from buildings: |  |  |  |  | 60775
B. Equipment removal from yard
|  | 1 | Wastewater recovery unit (101-BA) |  |  | each | 1 | 225 | 225
|  | 2 | Wastewater recovery unit (101-BB) |  |  | each | 1 | 225 | 225
|  | 3 | Wastewater recovery unit (101-BC) |  |  | each | 1 | 225 | 225
|  | 4 | Wastewater recovery unit (101-BD) |  |  | each | 1 | 225 | 225
|  | 5 | Boil-off gas heater (102-CA) |  |  | each | 1 | 750 | 750
|  | 6 | Boil-off gas heater (102-CB) |  |  | each | 1 | 750 | 750
|  | 7 | Fuel gas heater (103-CA) |  |  | each | 1 | 175 | 175
|  | 8 | Fuel gas heater (103-CB) |  |  | each | 1 | 175 | 175
|  | 9 | Purge gas heater (104-C) |  |  | each | 1 | 175 | 175
|  | 10 | Purge gas heater (105-CA) |  |  | each | 1 | 175 | 175
|  | 11 | Purge gas heater (105-CB) |  |  | each | 1 | 175 | 175
|  | 12 | Purge gas heater (106-CA) |  |  | each | 1 | 175 | 175
|  | 13 | Purge gas heater (106-CB) |  |  | each | 1 | 175 | 175
|  | 14 | Compressor intercooler (107, 108, 109, 110, 114-CA) |  |  | each | 1 | 350 | 350
|  | 15 | Compressor intercooler (107, 108, 109, 110, 114-CB) |  |  | each | 1 | 350 | 350
|  | 16 | Compressor intercooler (107, 108, 109, 110, 114-CC) |  |  | each | 1 | 350 | 350
|  | 17 | LNG vapor economizer (113-CA) |  |  | each | 1 | 550 | 550
|  | 18 | LNG vapor economizer (113-CB) |  |  | each | 1 | 550 | 550
|  | 19 | Purge gas heater (115-C) |  |  | each | 1 | 175 | 175
|  | 20 | Turbine generator cooling water cooler (116-CA) |  |  | each | 1 | 300 | 300
|  | 21 | Turbine generator cooling water cooler (116-CB) |  |  | each | 1 | 300 | 300
|  | 22 | Turbine generator cooling water cooler (116-CC) |  |  | each | 1 | 300 | 300
|  | 23 | Salt bath heater (117-C) |  |  | each | 1 | 325 | 325
|  | 24 | Fire water tank heater (118-C) |  |  | each | 1 | 175 | 175
[7 empty] | Subtotal this sheet: |  | 7350

## Onshore Dem 2
Exhibit No. DCP-27
Page 9 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
IV. | Onshore Demolition Work
Estimated
Cost
| B. Equipment removal from yard (continued) |  |  |  |  | Unit | No. | Unit Cost | (2006$)
|  | 25 | Booster pump surge tank (104-F) |  |  | each | 1 | 1200 | 1200
|  | 26 | Fuel gas scrubber (105-F) |  |  | each | 1 | 175 | 175
|  | 27 | Fuel gas scrubber (106-F) |  |  | each | 1 | 175 | 175
|  | 28 | Fire water storage tank (110-FA) |  |  | each | 1 | 12500 | 12500
|  | 29 | Fire water storage tank (110-FB) |  |  | each | 1 | 12500 | 12500
|  | 30 | Water storage tank (111-F) |  |  | each | 1 | 225 | 225
|  | 31 | Economizer water surge tank (112-F) |  |  | each | 1 | 275 | 275
|  | 32 | NG Vapor scrubber (114-F) |  |  | each | 1 | 650 | 650
|  | 33 | Emergency generator fuel tank (119-F) |  |  | each | 1 | 110 | 110
|  | 34 | Cooling water pump surge tank |  |  | each | 1 | 300 | 300
|  | 35 | Fire pump fuel tank (122-F) |  |  | each | 1 | 110 | 110
|  | 36 | Glycol tank (126-F) |  |  | each | 1 | 225 | 225
|  | 37 | Propane storage tank (127-F) |  |  | each | 1 | 400 | 400
|  | 38 | Vent stack (128-F) |  |  | each | 1 | 3200 | 3200
|  | 39 | Lube oil storage tank (129-F) |  |  | each | 1 | 300 | 300
|  | 40 | Lube oil storage tank (130-F) |  |  | each | 1 | 300 | 300
|  | 41 | LNG vaporizer exhaust blower (107-J) |  |  | each | 1 | 650 | 650
|  | 42 | Economizer water circulation pump (114-JA) |  |  | each | 1 | 220 | 220
|  | 43 | Economizer water circulation pump (114-JB) |  |  | each | 1 | 220 | 220
|  | 44 | Economizer water circulation pump (114-JC) |  |  | each | 1 | 220 | 220
|  | 45 | LNG liquid pump (115-J) |  |  | each | 1 | 150 | 150
|  | 46 | LNG liquid pump (115-JA) |  |  | each | 1 | 150 | 150
|  | 47 | Collection pond sump pump (118-JA) |  |  | each | 1 | 110 | 110
|  | 48 | Collection pond sump pump (118-JB) |  |  | each | 1 | 110 | 110
|  | 49 | Collection pond sump pump (119-JA) |  |  | each | 1 | 110 | 110
|  | 50 | Collection pond sump pump (118-JB) |  |  | each | 1 | 110 | 110
|  | 51 | Rollover pump (121-JA) |  |  | each | 1 | 110 | 110
|  | 52 | Rollover pump (121-JB) |  |  | each | 1 | 110 | 110
|  | 53 | Cooling water circulation pump (125-JA) |  |  | each | 1 | 175 | 175
|  | 54 | Cooling water circulation pump (125-JB) |  |  | each | 1 | 175 | 175
|  | 55 | Cooling water circulation pump (125-JC) |  |  | each | 1 | 175 | 175
|  | 56 | Well pump (128-J) |  |  | each | 1 | 360 | 360
|  | 57 | Glycol pump (134-J) |  |  | each | 1 | 110 | 110
|  | 58 | Propane loading pump (135-J) |  |  | each | 1 | 175 | 175
|  | 59 | Dewar tank (110-L) |  |  | each | 1 | 725 | 725
|  | 60 | Liquification unit (1995 vintage) |  | (same as ASU) |  |  |  | 366383
|  | 61 | Air separation unit (2003 vintage) |  | (20% of installation cost of $1,831,916) |  |  |  | 366383
|  | 62 | M&R facility (2003 vintage) |  | (Equivalent to removal of OX M&R) |  |  |  | 67411
[5 empty] | Subtotal this sheet: |  |  |  | 836987
|  |  |  | Total outdoor equipment removal: |  |  |  |  | 844337

## Onshore Dem 3
Exhibit No. DCP-27
Page 10 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
IV. | Onshore Demolition Work
Estimated
Cost
| C. Dismantle rigid frame buildings |  |  |  | Unit | No. | Unit Cost | (2006$)
|  | 1 | Booster pump building (103-H) |  | cf | 70000 | 0.37 | 25900
|  | 2 | LNG vaporizer building (104-H) |  | cf | 232000 | 0.37 | 85840
|  | 3 | Generator building (105-H) |  | cf | 168480 | 0.37 | 62337.6
|  | 4 | LNG vapor compressor building (106-H) |  | cf | 107100 | 0.37 | 39627
|  | 5 | Boil-off compressor building (107-H) |  | cf | 138600 | 0.37 | 51282
|  | 6 | Fire pump building (110-H) |  | cf | 13600 | 0.37 | 5032
|  | 7 | Warehouse building |  | cf | 54000 | 0.37 | 19980
[7 empty] | Subtotal: | 289998.6
|  |  | Markup by general contractor (15%) |  |  |  |  | 43499.79
|  |  |  | Total dismantle rigid frame buildings: |  |  |  | 333498.39
D. Purge, clean and dismantle LNG storage tanks
|  | 1 | Tank 101-FA (170' Dia x 139' high - 375,000 bbls) |  |  |  |  | 2968309.2388
|  | 2 | Tank 101-FB (170' Dia x 139' high - 375,000 bbls) |  |  |  |  | 2968309.2388
|  | 3 | Tank 101-FC (170' Dia x 139' high - 375,000 bbls) |  |  |  |  | 2968309.2388
|  | 4 | Tank 101-FD (170' Dia x 139' high - 375,000 bbls) |  |  |  |  | 2968309.2388
|  | 5 | Tank 101-FE (252' Dia x 157' high - 850,000 bbls) |  |  |  |  | 4850000
|  |  |  | Total LNG tank removal: |  |  |  | 16723236.9551
E. Asbestos siding removal and disposal
|  | 1 | Booster pump building (103-H) |  | sf | 7930 | 7 | 55510
|  | 2 | LNG vaporizer building (104-H) |  | sf | 25810 | 7 | 180670
|  | 3 | Generator building (105-H) (siding removed)
|  | 4 | LNG vapor compressor building (106-H) |  | sf | 12659 | 7 | 88613
|  | 5 | Boil-off compressor building (107-H) |  | sf | 15587 | 7 | 109109
|  | 6 | Fire pump building (110-H) |  | sf | 7620 | 7 | 53340
[7 empty] | Subtotal: | 487242
|  |  | Markup by general contractor (15%) |  |  |  |  | 73086.3
|  |  |  | Total asbestos siding removal and disposal: |  |  |  | 560328.3

## Onshore Dem 4
Exhibit No. DCP-27
Page 11 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
IV. | Onshore Demolition Work
Estimated
Cost
| F. Demolish masonary buildings |  |  |  |  | Unit | No. | Unit Cost | (2006$)
|  | 1 | Substation #1 (101-K) |  |  | cf | 61344 | 0.37 | 22697.28
|  | 2 | Substation #2 (102-K) |  |  | cf | 27258 | 0.37 | 10085.46
|  | 3 | Substation #3 (103-K) |  |  | cf | 16920 | 0.37 | 6260.4
|  | 4 | Substation #4 (104-K) |  |  | cf | 9768 | 0.37 | 3614.16
|  | 5 | Building 108-K |  |  | cf | 2808 | 0.37 | 1038.96
|  | 6 | Building 110-K |  |  | cf | 2496 | 0.37 | 923.52
|  | 7 | Administrative building |  |  | cf | 102600 | 0.37 | 37962
|  | 8 | Maintenance building |  |  | cf | 110700 | 0.37 | 40959
|  | 9 | Garage building |  |  | cf | 39900 | 0.37 | 14763
|  | 10 | Gate building |  |  | cf | 7200 | 0.37 | 2664
|  | 11 | Tunnel venilation building |  |  | cf | 15840 | 0.37 | 5860.8
|  |  |  | Total demolish masonary buildings: |  |  |  |  | 146828.58
G. Disposal costs
|  | 1 | Masonary building materials disposal |  |  | container | 35.3 | 500 | 17650
|  | 2 | Rigid frame building |  | (recycler accepts scap on site)
|  | 3 | Piping material |  | (recycler accepts scap on site)
|  | 4 | Electrical power cable |  | (recycler accepts scap on site)
|  | 5 | Electrical switch gear |  | (recycler accepts scap on site)
|  | 6 | Misc. electrical, conduit, fittings & wire |  |  | container | 20 | 500 | 10000
|  | 7 | Pipe insulation |  |  | container | 15 | 500 | 7500
|  | 8 | Security fence |  |  | container | 5 | 500 | 2500
|  |  |  | Total disposal costs: |  |  |  |  | 37650

## Onshore Dem 5
Exhibit No. DCP-27
Page 12 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
IV. | Onshore Demolition Work
Estimated
Cost
| H. Pipe removal |  |  |  | Unit | No. | Unit Cost | (2006$)
|  | 1 | Removal of insulation
|  |  | a. | 2" and smaller pipe | ft | 1000 | 3.2 | 3200
|  |  | b. | 3" | ft | 500 | 3.25 | 1625
|  |  | c. | 4" | ft | 350 | 3.25 | 1137.5
|  |  | d. | 6" | ft | 2200 | 3.25 | 7150
|  |  | e. | 8" | ft | 700 | 3.85 | 2695
|  |  | f. | 10" | ft | 300 | 3.85 | 1155
|  |  | g. | 12" | ft | 850 | 3.85 | 3272.5
|  |  | h. | 14" | ft | 4020 | 4.6 | 18492
|  |  | i. | 16" | ft | 1500 | 4.6 | 6900
|  |  | j. | 18" | ft | 1500 | 5.45 | 8175
|  |  | k. | 20" | ft | 1400 | 5.45 | 7630
|  |  | l. | 24" | ft | 3700 | 5.45 | 20165
|  |  | m. | 30" | ft | 150 | 5.45 | 817.5
|  |  | n. | 32" | ft | 3900 | 5.45 | 21255
|  |  | o. | 36" | ft | 170 | 5.45 | 926.5
[7 empty] | Subtotal: | 104596
|  | 2 | Remove carbon steel pipe
|  |  | a. | 2" and smaller pipe | ft | 15200 | 0.5 | 7600
|  |  | b. | 3" | ft | 10900 | 0.95 | 10355
|  |  | c. | 4" | ft | 5900 | 1.25 | 7375
|  |  | d. | 6" | ft | 6600 | 1.9 | 12540
|  |  | e. | 8" | ft | 2000 | 2.45 | 4900
|  |  | f. | 10" | ft | 750 | 3.1 | 2325
|  |  | g. | 12" | ft | 2200 | 3.7 | 8140
|  |  | h. | 14" | ft | 100 | 4.25 | 425
|  |  | i. | 16" | ft | 220 | 4.95 | 1089
|  |  | j. | 18" | ft | 3300 | 5.5 | 18150
|  |  | k. | 20" | ft | 1000 | 6.15 | 6150
|  |  | l. | 24" | ft | 2300 | 7.4 | 17020
|  |  | m. | 30" | ft | 130 | 9.2 | 1196
|  |  | n. | 36" | ft | 0 | 11 | 0
[7 empty] | Subtotal: | 97265
|  | 3 | Remove stainless steel pipe
|  |  | a. | 2" and smaller pipe | ft | 1000 | 0.5 | 500
|  |  | b. | 3" | ft | 500 | 0.95 | 475
|  |  | c. | 4" | ft | 350 | 1.25 | 437.5
|  |  | d. | 6" | ft | 2200 | 1.9 | 4180
|  |  | e. | 8" | ft | 700 | 2.45 | 1715
|  |  | f. | 10" | ft | 300 | 3.1 | 930
[6 empty] | Subtotal this sheet: |  | 8237.5

## Onshore Dem 6
Exhibit No. DCP-27
Page 13 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
IV. | Onshore Demolition Work
Estimated
Cost
| H. Pipe removal (continued) | [5 empty] | Unit | No. | Unit Cost | (2006$)
|  | 3 | Remove stainless steel pipe (continued)
|  |  | g. | 12" | ( 850 ft) |  | ft | 850 | 3.7 | 3145
|  |  | h. | 14" | (4,020 ft) |  | ft | 4020 | 4.25 | 17085
|  |  | i. | 16" | (1,500 ft) |  | ft | 1500 | 4.95 | 7425
|  |  | j. | 18" | (1,500 ft) |  | ft | 1500 | 5.5 | 8250
|  |  | k. | 20" | (1,400 ft) |  | ft | 1400 | 6.15 | 8610
|  |  | l. | 24" | (3,700 ft) |  | ft | 3700 | 7.4 | 27380
|  |  | m. | 30" | ( 150 ft) |  | ft | 150 | 9.2 | 1380
|  |  | n. | 32" | (3,900 ft) |  | ft | 3900 | 9.8 | 38220
|  |  | o. | 36" | ( 170 ft) |  | ft | 170 | 11 | 1870
[8 empty] | Subtotal this sheet: |  | 113365
[6 empty] | Total: |  |  |  | 121602.5
|  | 4 | Remove large valves |  |  |  | L.S. |  |  | 23200
[9 empty] | Subtotal: | 23200
[5 empty] | Total pipe removal: |  |  | 0 | 1.45 | 346663.5
I. Site work
|  | 1 | Remove fence |  |  |  | ft | 13300 | 2 | 26600
|  | 2 | Remove & dispose of asphalt pavement |  |  |  | sy | 53750 | 5 | 268750
|  | 3 | Remove light pole fixtures |  |  |  | each | 150 | 100 | 15000
|  | 4 | Breakdown 4 smaller LNG storage tank dikes |  |  |  | cy | 38000 | 15 | 570000
|  | 5 | Breakdown Tank E storage tank dikes |  |  |  | cy | 21500 | 15 | 322500
|  | 6 | Fill & seal onshore tunnel entrance shaft |  |  |  | cy | 900 | 30 | 27000
|  | 7 | Breakup concrete pads walls, etc. |  |  |  | cf | 2720 | 4 | 10880
|  | 8 | Earthwork for leveling and covering |  |  |  | cy | 50000 | 15 | 750000
|  | 9 | Remove fire hydrants |  |  |  | each | 15 | 220 | 3300
|  | 10 | Above ground roadway structures |  |  |  | L.S. |  |  | 10000
[5 empty] | Total site work: |  |  |  |  | 2004030
J. Removal of misc. steel structures
|  | 1 | Pipe sleepers |  |  |  | ton | 37 | 620 | 22940
|  | 2 | Misc. steel |  |  |  | ton | 53 | 58 | 3074
[5 empty] | Total remove misc. structures: |  |  |  |  | 26014
K. Cap TL-522
|  | 1 | Cap 36-inch send out line |  |  |  | L.S. |  |  | 15000
[5 empty] | Total pipeline abandonment: |  |  |  |  | 15000
L. Power cable removal
|  | 1 | Remove insulated elecrical power cable |  |  |  | ft | 31300 | 0.3 | 9390
[5 empty] | Total power cable removal: |  |  |  |  | 9390

## Offshore Dem 1
Exhibit No. DCP-27
Page 14 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
A. Phase 1
1. Removal of equipment
Estimated
Cost
|  | a. | Dismantle equipment (equipment removal crew) |  | Unit | No. | Unit Cost | (2006$)
|  | 1 |  | North unloading arms | day | 1 | 5614.16 | 5614.16
|  | 2 |  | South unloading arms | day | 1 | 5614.16 | 5614.16
|  | 3 |  | North survival capsule davit | day | 0.125 | 5614.16 | 701.77
|  | 4 |  | South survival capsule davit | day | 0.125 | 5614.16 | 701.77
|  | 5 |  | North crane disassembly | day | 1 | 5614.16 | 5614.16
|  | 6 |  | South crane disassembly | day | 1 | 5614.16 | 5614.16
|  | 7 |  | Disassemble operations platform w platform crane | day | 1 | 5614.16 | 5614.16
|  | 8 |  | Operations survival capsule davit | day | 0.125 | 5614.16 | 701.77
|  | 9 |  | Heater (111-CA) | day | 0.125 | 5614.16 | 701.77
|  | 10 |  | Heater (112-CA) | day | 0.125 | 5614.16 | 701.77
|  | 11 |  | LNG pumps (101-JA thru 101-JF) | day | 1 | 5614.16 | 5614.16
|  | 12 |  | Horizontal vessel (102-FA) | day | 0.5 | 5614.16 | 2807.08
|  | 13 |  | Horizontal vessel (103-FA) | day | 0.5 | 5614.16 | 2807.08
|  | 14 |  | Dry chemical Unit (115-LA) | day | 0.125 | 5614.16 | 701.77
|  | 15 |  | Dry chemical Unit (115-LB) | day | 0.125 | 5614.16 | 701.77
|  | 16 |  | Heater (111-CB) | day | 0.125 | 5614.16 | 701.77
|  | 17 |  | Heater (112-CB) | day | 0.125 | 5614.16 | 701.77
|  | 18 |  | LNG pumps (102-JA thru 102-JF) | day | 1 | 5614.16 | 5614.16
|  | 19 |  | Horizontal vessel (102-FB) | day | 0.5 | 5614.16 | 2807.08
|  | 20 |  | Horizontal vessel (103-FB) | day | 0.5 | 5614.16 | 2807.08
|  | 21 |  | Dry chemical unit (115-LC) | day | 0.125 | 5614.16 | 701.77
|  | 22 |  | Dry chemical unit (115-LD) | day | 0.125 | 5614.16 | 701.77
|  | 23 |  | Vertical fire water pump (109-J) | day | 1 | 5614.16 | 5614.16
|  | 24 |  | Vertical fire water pump (109-JA) | day | 1 | 5614.16 | 5614.16
|  | 25 |  | Emergency generator (120-J) | day | 1 | 5614.16 | 5614.16
|  | 26 |  | LNG liquid pump (122-JA) | day | 0.125 | 5614.16 | 701.77
|  | 27 |  | LNG liquid pump (122-JB) | day | 0.125 | 5614.16 | 701.77
|  | 28 |  | Pumps (123-JA) | day | 0.125 | 5614.16 | 701.77
|  | 29 |  | Pumps (123-JB) | day | 0.125 | 5614.16 | 701.77
|  | 30 |  | Pumps (123-JC) | day | 0.125 | 5614.16 | 701.77
|  | 31 |  | Potable water pumps (130-J) | day | 0.125 | 5614.16 | 701.77
|  | 32 |  | Dewar tank (109-L) | day | 0.125 | 5614.16 | 701.77
|  | 33 |  | Diesel fuel tank (123-F) | day | 0.125 | 5614.16 | 701.77
|  | 34 |  | Diesel fuel tank (124-F) | day | 0.125 | 5614.16 | 701.77
|  | 35 |  | Sewage Tank (125-F) | day | 0.5 | 5614.16 | 2807.08
|  | 36 |  | Dismantle structural steel north unloading plf | day | 1 | 5614.16 | 5614.16
|  | 37 |  | Dismantle structural steel south unloading plf | day | 1 | 5614.16 | 5614.16
|  | 38 |  | Dismantle office building 120-K | day | 5.5 | 5614.16 | 30877.88
|  | 39 |  | Remove gangways, stairs, misc structures | day | 20 | 5614.16 | 112283.2
|  | 40 |  | Dismantle breasting dolphin top works | day | 4 | 5614.16 | 22456.64
[7 empty] | Subtotal: | 261058.44

## Offshore Dem 2
Exhibit No. DCP-27
Page 15 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
A. Phase 1
1. Removal of equipment (cont.)
Estimated
|  | b. | Load equipment onto barge from north pier |  |  |  |  | Cost
|  |  | using small crane barge (50T) |  | Unit | No. | Unit Cost | (2006$)
|  | 1 |  | Mobilization of small crane spread | day | 2 | 42400 | 84800
|  | 2 |  | Horizontal vessel (102-FA) | day | 0.25 | 42400 | 10600
|  | 3 |  | Horizontal vessel (103-FA) | day | 0.25 | 42400 | 10600
|  | 4 |  | Structural steel from north platform | day | 0.25 | 42400 | 10600
|  | 5 |  | Load north crane onto barge | day | 0.5 | 42400 | 21200
|  | 6 |  | Load north unloading arms | day | 0.5 | 42400 | 21200
|  | 7 |  | Load misc. small equipment | day | 1 | 42400 | 42400
|  | 8 |  | Assist with removal of breasting dolphin tops | day | 1 | 42400 | 42400
|  | 9 |  | Reposition of barge | day | 0.5 | 42400 | 21200
[6 empty] | Subtotal: |  | 265000
|  | c. | Load equipment onto barge from south pier
using small crane barge (50T)
|  | 1 |  | Horizontal vessel (102-FB) | day | 0.25 | 42400 | 10600
|  | 2 |  | Horizontal vessel (103-FB) | day | 0.25 | 42400 | 10600
|  | 3 |  | Structural steel from south platform | day | 0.25 | 42400 | 10600
|  | 4 |  | Load south crane unto barge | day | 0.5 | 42400 | 21200
|  | 5 |  | Load south unloading arms | day | 0.5 | 42400 | 21200
|  | 6 |  | Load misc. small equipment | day | 1 | 42400 | 42400
|  | 7 |  | Assist with removal of breasting dolphin tops | day | 1 | 42400 | 42400
|  | 8 |  | Reposition of barge | day | 0.5 | 42400 | 21200
[6 empty] | Subtotal: |  | 180200
|  | d. | Load equipment onto barge from
operation platform using small crane barge (50T)
|  | 1 |  | Load operation cranes onto barge | day | 0.33333 | 42400 | 14133.3333
|  | 2 |  | Load misc. small equipment | day | 1 | 42400 | 42400
|  | 3 |  | Load construction equipment onto barge | day | 2 | 42400 | 84800
|  | 4 |  | Demobilization of small crane spread | day | 2 | 42400 | 84800
[6 empty] | Subtotal: |  | 226133.3333
|  |  |  | Total cost of equipment removal: |  |  |  | 932391.7733

## Offshore Dem 3
Exhibit No. DCP-27
Page 16 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
A. Phase 1
2. Pipe Removal (deck crews)
Estimated
Cost
|  | a. | Removal of insulation (laborer crew) |  |  | Unit | No. | Unit Cost | (2006$)
|  | 1 |  | 2-inch pipe | (40 ft) | day | 0.2 | 2885.76 | 577.152
|  | 2 |  | 4-inch pipe | (400 ft) | day | 1.3 | 2885.76 | 3751.488
|  | 3 |  | 6-inch pipe | (300 Ft) | day | 1 | 2885.76 | 2885.76
|  | 4 |  | 8-inch pipe | (2800 ft) | day | 10.3 | 2885.76 | 29723.328
|  | 5 |  | 10-inch pipe | (110 ft) | day | 0.4 | 2885.76 | 1154.304
|  | 6 |  | 12-inch pipe | (250 ft) | day | 0.9 | 2885.76 | 2597.184
|  | 7 |  | 14-inch pipe | (2650 ft) | day | 11.75 | 2885.76 | 33907.68
|  | 8 |  | 16-inch pipe | (250 ft) | day | 1.1 | 2885.76 | 3174.336
|  | 9 |  | 24-inch pipe | (50 ft) | day | 0.2 | 2885.76 | 577.152
|  | 10 |  | 32-inch pipe | (2200 ft) | day | 11.2 | 2885.76 | 32320.512
[7 empty] | Subtotal: |  | 110668.896
|  | b. | Removal of carbon steel pipe (pipe removal crew)
|  | 1 |  | 2-inch pipe | (2500 ft) | day | 0.8 | 5614.16 | 4491.328
|  | 2 |  | 3-inch pipe | (5500 ft) | day | 3.5 | 5614.16 | 19649.56
|  | 3 |  | 4-inch pipe | (300 ft) | day | 0.3 | 5614.16 | 1684.248
|  | 4 |  | 6-inch pipe | (600 ft) | day | 0.8 | 5614.16 | 4491.328
[7 empty] | Subtotal: |  | 30316.464
|  | c. | Removal of stainless steel pipe (pipe removal crew)
|  | 1 |  | 2-inch pipe | (40 ft) | day | 0.1 | 5614.16 | 561.416
|  | 2 |  | 4-inch pipe | (400 ft) | day | 0.4 | 5614.16 | 2245.664
|  | 3 |  | 6-inch pipe | (300 ft) | day | 0.4 | 5614.16 | 2245.664
|  | 4 |  | 8-inch pipe | (2800 ft) | day | 4.8 | 5614.16 | 26947.968
|  | 5 |  | 10-inch pipe | (110 ft) | day | 0.4 | 5614.16 | 2245.664
|  | 6 |  | 12-inch pipe | (250 ft) | day | 0.65 | 5614.16 | 3649.204
|  | 7 |  | 14-inch pipe | (2650 ft) | day | 8 | 5614.16 | 44913.28
|  | 8 |  | 16-inch pipe | (250 ft) | day | 0.9 | 5614.16 | 5052.744
|  | 9 |  | 24-inch pipe | (50 ft) | day | 0.2 | 5614.16 | 1122.832
|  | 10 |  | 32-inch pipe | (2200 ft) | day | 14.75 | 5614.16 | 82808.86
[7 empty] | Subtotal: |  | 171793.296
|  |  |  | Total pipe removal cost: |  |  |  |  | 312778.656

## Offshore Dem 4
Exhibit No. DCP-27
Page 17 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
A. Phase 1
3. Removal of Electrical Cable (laborer crew)
Estimated
Cost
[6 empty] | Unit | No. | Unit Cost | (2006$)
|  | a. | Remove cable | (2000 ft) |  | day | 1 | 2885.76 | 2885.76
|  |  | Total cost of cable removal: | [5 empty] | 2885.76
4. Disposal of Pipe and Equipment
|  | a. | Load material and equipment (50 Ton barge) |  |  | day | 4 | 42400 | 169600
|  | b. | Load mat. and equip. (laborer crew) |  |  | day | 4 | 2885.76 | 11543.04
|  | c. | Demob materials (tug and barge day rate) |  |  | day | 2 | 8600 | 17200
|  | d. | Unload barges (tug and barge day rate) |  |  | day | 2 | 8600 | 17200
|  | e. | Unload and dispose of insulation |  |  | container | 6 | 500 | 3000
|  | f. | Barge unloading costs |  |  | barge | 2 | 10000 | 20000
[5 empty] | Total disposal cost: |  |  |  | 238543.04

## Offshore Dem 5
Exhibit No. DCP-27
Page 18 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
B. Phase 2
1. Removal of pipe trestle, roadway panel, and roadway beams
|  |  | (Production rate 8 hours per panel, trestle, or road beam) |  |  |  | Estimated
Cost
|  |  |  | Unit | No. | Unit Cost | (2006$)
|  | a. | Mob/demob of 250 ton barge spread | day | 4 | 61800 | 247200
|  | b. | N. unloading platform access road panel 1 | day | 0.33333 | 61800 | 20600
|  | c. | N. unloading platform access road beams | day | 0.33333 | 61800 | 20600
|  | d. | N. unloading platform pipe trestle | day | 0.33333 | 61800 | 20600
|  | e. | N. unloading platform access road elbow | day | 0 | 61800 | 0
|  | f. | 3N-4N access road panel | day | 0.33333 | 61800 | 20600
|  | g. | 3N-4N access road beams | day | 0.33333 | 61800 | 20600
|  | h. | 3N-4N access pipe trestle | day | 0.33333 | 61800 | 20600
|  | i. | 4N-5N access road panel | day | 0.33333 | 61800 | 20600
|  | j. | 4N-5N access road beams | day | 0.33333 | 61800 | 20600
|  | k. | 4N-5N access pipe trestle | day | 0.33333 | 61800 | 20600
|  | l. | 5N-6N access road panel | day | 0.33333 | 61800 | 20600
|  | m. | 5N-6N access road beams | day | 0.33333 | 61800 | 20600
|  | n. | 5N-6N access pipe trestle | day | 0.33333 | 61800 | 20600
|  | o. | 6N-7N access road panel | day | 0.33333 | 61800 | 20600
|  | p. | 6N-7N access road beams | day | 0.33333 | 61800 | 20600
|  | q. | 6N-7N access pipe trestle | day | 0.33333 | 61800 | 20600
|  | r. | N. service platform access road panel | day | 0.33333 | 61800 | 20600
|  | s. | N. service platform access road beams | day | 0.33333 | 61800 | 20600
|  | t. | 7N-8N access road and pipe panel | day | 0 | 61800 | 0
|  | u. | 8N-9N access road and pipe panel | day | 0 | 61800 | 0
|  | v. | 9N-10N access road panel | day | 0 | 61800 | 0
|  | w. | 9N-10N access road beams | day | 0.33333 | 61800 | 20600
|  | x. | 9N-10N access pipe trestle | day | 0.33333 | 61800 | 20600
|  | y. | 10N-11N access road panel | day | 0.33333 | 61800 | 20600
|  | z. | 10N-11N access road beams | day | 0.33333 | 61800 | 20600
|  | aa. | 10N-11N access pipe trestle | day | 0.33333 | 61800 | 20600
|  | ab. | 11N-12N access road panel | day | 0.33333 | 61800 | 20600
|  | ac. | 11N-12N access road beams | day | 0.33333 | 61800 | 20600
|  | ad. | 11N-12N access pipe trestle | day | 0.33333 | 61800 | 20600
|  | ae. | 12N-13N access road panel | day | 0.33333 | 61800 | 20600
|  | af. | 12N-13N access road beams | day | 0.33333 | 61800 | 20600
|  | ag. | 12N-13N access pipe trestle | day | 0.33333 | 61800 | 20600
|  | ah. | Center T head | day | 0 | 61800 | 0
|  | ai. | Center T head pipe support deck | day | 0 | 61800 | 0
|  | aj. | Center T head pipe roadway deck | day | 0 | 61800 | 0
|  | ak. | JN-15N pipe support trestle | day | 0.33333 | 61800 | 20600
[5 empty] | Subtotal this sheet: |  | 844600

## Offshore Dem 6
Exhibit No. DCP-27
Page 19 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
B. Phase 2
1. Removal of pipe trestle, roadway panel, and roadway beam (continued)
|  |  | (Production rate 8 hours per panel, trestle, or road beam) |  |  |  | Estimated
Cost
|  |  |  | Unit | No. | Unit Cost | (2006$)
|  | al. | 15N-AN pipe support trestle | day | 0.33333 | 61800 | 20600
|  | am. | J-15 access road panel | day | 0.33333 | 61800 | 20600
|  | an. | 15-A access road panel | day | 0.33333 | 61800 | 20600
|  | ao. | JS-15S pipe support trestle | day | 0.33333 | 61800 | 20600
|  | ap. | 15S-AS pipe support trestle | day | 0.33333 | 61800 | 20600
|  | aq. | S. unloading platform access road panel 1 | day | 0.33333 | 61800 | 20600
|  | ar. | S. unloading platform access road beams | day | 0.33333 | 61800 | 20600
|  | as. | S. unloading platform pipe trestle | day | 0.33333 | 61800 | 20600
|  | at. | S. unloading platform access road elbow | day | 0 | 61800 | 0
|  | au. | 3S-4S access road panel | day | 0.33333 | 61800 | 20600
|  | av. | 3S-4S access road beams | day | 0.33333 | 61800 | 20600
|  | aw. | 3S-4S access pipe trestle | day | 0.33333 | 61800 | 20600
|  | ax. | 4S-5S access road panel | day | 0.33333 | 61800 | 20600
|  | ay. | 4S-5S access road beams | day | 0.33333 | 61800 | 20600
|  | az. | 4S-5S access pipe trestle | day | 0.33333 | 61800 | 20600
|  | ba. | 5S-6S access road panel | day | 0.33333 | 61800 | 20600
|  | bb. | 5S-6S access road beams | day | 0.33333 | 61800 | 20600
|  | bc. | 5S-6S access pipe trestle | day | 0.33333 | 61800 | 20600
|  | bd. | 6S-7S access road panel | day | 0.33333 | 61800 | 20600
|  | be. | 6S-7S access road beams | day | 0.33333 | 61800 | 20600
|  | bf. | 6S-7S access pipe trestle | day | 0.33333 | 61800 | 20600
|  | bg. | S. service platform access road panel | day | 0.33333 | 61800 | 20600
|  | bh. | S. service platform access road beams | day | 0.33333 | 61800 | 20600
|  | bi. | 7S-8S access road and pipe panel | day | 0.33333 | 61800 | 20600
|  | bj. | 8S-9S access road and pipe panel | day | 0.33333 | 61800 | 20600
|  | bk. | 9S-10S access road panel | day | 0 | 61800 | 0
|  | bl. | 9S-10S access road beams | day | 0 | 61800 | 0
|  | bm. | 9S-10S access pipe trestle | day | 0 | 61800 | 0
|  | bn. | 10S-11S access road panel | day | 0.33333 | 61800 | 20600
|  | bo. | 10S-11S access road beams | day | 0.33333 | 61800 | 20600
|  | bp. | 10S-11S access pipe trestle | day | 0.33333 | 61800 | 20600
|  | bq. | 11S-12S access road panel | day | 0.33333 | 61800 | 20600
|  | br. | 11S-12S access road beams | day | 0.33333 | 61800 | 20600
|  | bs. | 11S-12S access pipe trestle | day | 0.33333 | 61800 | 20600
|  | bt. | 12S-13S access road panel | day | 0.33333 | 61800 | 20600
|  | bu. | 12S-13S access road beams | day | 0.33333 | 61800 | 20600
|  | bv. | 12S-13S access pipe trestle | day | 0.33333 | 61800 | 20600
[5 empty] | Subtotal this sheet: |  | 679800
|  | Total removal cost pipe trestle, rdwy panel, and rdway beam: |  |  |  |  | 1524400

## Offshore Dem 7
Exhibit No. DCP-27
Page 20 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
B. Phase 2
2. Breakup of deck platforms (concrete demolition crew)
Estimated
Cost
[6 empty] | Unit | No. | Unit Cost | (2006$)
|  | a. |  | N. unloading platform access road elbow |  | day | 5 | 4703.36 | 23516.8
|  | b. |  | S. unloading platform access road elbow |  | day | 5 | 4703.36 | 23516.8
|  | c. |  | N. unloading platform |  | day | 15 | 4703.36 | 70550.4
|  | d. |  | S. unloading platform |  | day | 15 | 4703.36 | 70550.4
|  | e. |  | N. service platform |  | day | 5 | 4703.36 | 23516.8
|  | f. |  | S. service platform |  | day | 5 | 4703.36 | 23516.8
|  | g. |  | N. access road platform (@ service platform) |  | day | 5 | 4703.36 | 23516.8
|  | h. |  | S. access road platform (@ service platform) |  | day | 5 | 4703.36 | 23516.8
|  | i. |  | Center T-head platform |  | day | 10 | 4703.36 | 47033.6
|  | j. |  | Operations platform |  | day | 20 | 4703.36 | 94067.2
[5 empty] | Total cost of platform breakup: |  |  |  | 423302.4
B. Phase II
3. Removal and disposal of deck platforms (revolving crane barge 100 Ton)
|  | a. |  | Mob/demob of revolving crane spread |  | day | 4 | 61800 | 247200
|  | b. |  | N. unloading platform access road elbow |  | day | 2 | 61800 | 123600
|  | c. |  | S. unloading platform access road elbow |  | day | 2 | 61800 | 123600
|  | d. |  | N. unloading platform |  | day | 7 | 61800 | 432600
|  | e. |  | S. unloading platform |  | day | 7 | 61800 | 432600
|  | f. |  | N. service platform |  | day | 3 | 61800 | 185400
|  | g. |  | S. service platform |  | day | 3 | 61800 | 185400
|  | h. |  | N. access road platform (@ service platform) |  | day | 2 | 61800 | 123600
|  | i. |  | S. access road platform (@ service platform) |  | day | 2 | 61800 | 123600
|  | j. |  | Center T-head platform |  | day | 4 | 61800 | 247200
|  | k. |  | Operations platform |  | day | 8 | 61800 | 494400
[5 empty] | Total cost of removal of deck platforms: |  |  |  | 2719200
B. Phase II
4. Removal of walkways (revolving crane barge 100 Ton)
(production rate 12 hours to remove one walkway)
|  |  | a. | Walkways between MD-1N & MD-2N |  | day | 1 | 61800 | 61800
|  |  | b. | Walkway between MD-2N & MD-3N |  | day | 0.5 | 61800 | 30900
|  |  | c. | Walkway between MD-3N & N loading platform |  | day | 0.5 | 61800 | 30900
|  |  | d. | Walkway to bresting dolphin BD-1N |  | day | 0.5 | 61800 | 30900
|  |  | e. | Walkway to bresting dolphin BD-4N |  | day | 0.5 | 61800 | 30900
[7 empty] | Subtotal this sheet: |  | 185400

## Offshore Dem 8
Exhibit No. DCP-27
Page 21 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
B. Phase 2
4. Removal of walkways (continued)
|  |  | (production rate 12 hours to remove one walkway) |  |  |  |  | Estimated
Cost
[5 empty] | Unit | No. | Unit Cost | (2006$)
|  | f. | Walkway to bresting dolphin BD-5N |  | day | 0.5 | 61800 | 30900
|  | g. | Walkway to bresting dolphin BD-5S |  | day | 0.5 | 61800 | 30900
|  | h. | Walkway to bresting dolphin BD-4S |  | day | 0.5 | 61800 | 30900
|  | i. | Walkway to bresting dolphin BD-1S |  | day | 0.5 | 61800 | 30900
|  | j. | Walkway between MD 3S & S. loading platform |  | day | 0.5 | 61800 | 30900
|  | k. | Walkway between MD 2S & MD-3S |  | day | 0.5 | 61800 | 30900
|  | l. | Walkways between MD-1S & MD-2S |  | day | 1 | 61800 | 61800
[6 empty] | Subtotal this sheet: |  | 247200
|  |  |  | Total cost of walkway removal: |  |  |  | 432600
B. Phase II Removal of walkways, roadways, trestles
5. Removal of mooring dolphin caps (revolving crane barge 100 Ton)
(production rate 24 hours to remove one mooring dolphin cap)
|  | a. | Breakup and removal of MD-1N cap |  | day | 1 | 61800 | 61800
|  | b. | Breakup and removal of MD-2N cap |  | day | 1 | 61800 | 61800
|  | c. | Breakup and removal of MD-3N cap |  | day | 1 | 61800 | 61800
|  | d. | Breakup and removal of MD-4N cap |  | day | 1 | 61800 | 61800
|  | e. | Breakup and removal of MD-5N cap |  | day | 1 | 61800 | 61800
|  | f. | Breakup and removal of MD-6 cap |  | day | 1 | 61800 | 61800
|  | g. | Breakup and removal of MD-5S cap |  | day | 1 | 61800 | 61800
|  | h. | Breakup and removal of MD-4S cap |  | day | 1 | 61800 | 61800
|  | i. | Breakup and removal of MD-3S cap |  | day | 1 | 61800 | 61800
|  | j. | Breakup and removal of MD-2S cap |  | day | 1 | 61800 | 61800
|  | k. | Breakup and removal of MD-1S cap |  | day | 1 | 61800 | 61800
|  |  |  | Total cost to remove mooring dolphin caps: |  |  |  | 679800

## Offshore Dem 9
Exhibit No. DCP-27
Page 22 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
C. Phase 3
1. Pile cap cutting
|  |  | (Using abrasive water jet cutting equipment) | [9 empty] | Estimated
Cost
[10 empty] | Unit | No. | Unit Cost | (2006$)
|  | a. |  | North unloading platform - Row D cap |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | b. |  | North unloading platform - Row E cap |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | c. |  | N. Roadway cap at 3N |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | d. |  | N. Roadway cap at 4N |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | e. |  | N. Roadway cap at 5N |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | f. |  | N. Roadway cap at 6N |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | g. |  | N. Roadway cap at 7N |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | h. |  | N. Roadway cap at 8N |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | i. |  | N. Roadway cap at 9N |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | j. |  | N. Roadway cap at 10N |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | k. |  | N. Roadway cap at 11N |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | l. |  | N. Roadway cap at 12N |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | m. |  | Center tee deck - 13N cap |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | n. |  | Center tee deck - 13S cap |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | o. |  | Center tee deck - J cap |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | p. |  | Connecting trestle/roadway cap - Row 15 |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | q. |  | Operations platform deck - cap @ Row A |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | r. |  | S. Roadway cap at 12S |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | s. |  | S. Roadway cap at 11S |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | t. |  | S. Roadway cap at 10S |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | u. |  | S. Roadway cap at 9S |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | v. |  | S. Roadway cap at 8S |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | w. |  | S. Roadway cap at 7S |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | x. |  | S. Roadway cap at 6S |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | y. |  | S. Roadway cap at 5S |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | z. |  | S. Roadway cap at 4S |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | aa. |  | S. Roadway cap at 3S |  |  |  | 1 | cut | day | 1 | 10000 | 10000
|  | ab. |  | South unloading platform - Row D cap |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | ac. |  | South unloading platform - Row E cap |  |  |  | 2 | cuts | day | 2 | 10000 | 20000
|  | ad. |  | Mob/demob of equipment | [5 empty] | day | 4 | 10000 | 40000
[5 empty] | Total cost of pipe cap cutting: | [7 empty] | 460000
C. Phase III
2. Pile cutting
(Using abrasive water jet cutting equipment)
|  | a. |  | 54-inch concrete piles |  | 194 | piles (5.4 hr/pile) |  |  | day | 43.65 | 10000 | 436500
|  | b. |  | 36-inch concrete piles |  | 20 | piles (3.6 hr/pile) |  |  | day | 3 | 10000 | 30000
|  | c. |  | 30-inch steel piles |  | 78 | piles (3.0 hr/pile) |  |  | day | 9.75 | 10000 | 97500
|  | d. |  | 42-inch steel piles |  | 48 | piles (4.2 hr/pile) |  |  | day | 8.4 | 10000 | 84000
|  | e. |  | 18-inch steel piles |  | 31 | piles (1.8 hr/pile) |  |  | day | 2.32 | 10000 | 23200
[5 empty] | Total cost to cut piles: | [7 empty] | 671200

## Offshore Dem 10
Exhibit No. DCP-27
Page 23 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
C. Phase 3
3. Tunnel access shaft removal
|  |  | ( using abrasive cutting equip. and shear leg crane) | [9 empty] | Estimated
Cost
[10 empty] | Unit | No. | Unit Cost | (2006$)
|  | a. |  | Cut #1 for upper shaft section removal | [5 empty] | ft | 90 | 1000 | 90000
|  | b. |  | Cut #2 for upper shaft section removal | [5 empty] | ft | 90 | 1000 | 90000
|  | c. |  | Cut #3 internal cut for lower shaft section removal | [5 empty] | ft | 90 | 1000 | 90000
|  | d. |  | Cut #3 underwater cut for lower shaft section removal | [5 empty] | ft | 90 | 1000 | 90000
|  | e. |  | Cut #4 internal cut for lower shaft section removal | [5 empty] | ft | 90 | 1000 | 90000
|  | f. |  | Cut #4 underwater cut for lower shaft section removal | [5 empty] | ft | 90 | 1000 | 90000
|  | g. |  | Shear leg crane (4 lifts) | [5 empty] | day | 4 | 61800 | 247200
[5 empty] | Total cost to remove tunnel access shaft: | [7 empty] | 787200
C. Phase 3
4. Pile removal
|  | a. |  | Using 100 ton revolving crane or shear leg crane
|  | 1 |  | Mobilization of revolving crane | [5 empty] | day | 2 | 61800 | 123600
|  | 2 |  | Mooring dolphin 1N |  | 3 | hr/pile | 10 | (30-in steel) | day | 1.25 | 61800 | 77250
|  | 3 |  | Mooring dolphin 2N |  | 3 | hr/pile | 6 | (30-in steel) | day | 0.75 | 61800 | 46350
|  | 4 |  | Mooring dolphin 3N |  | 3 | hr/pile | 6 | (30-in steel) | day | 0.75 | 61800 | 46350
|  | 5 |  | Mooring dolphin 4N |  | 3 | hr/pile | 6 | (30-in steel) | day | 0.75 | 61800 | 46350
|  | 6 |  | Mooring dolphin 5N |  | 3 | hr/pile | 6 | (30-in steel) | day | 0.75 | 61800 | 46350
|  | 7 |  | Mooring dolphin 6 |  | 3 | hr/pile | 10 | (30-in steel) | day | 1.25 | 61800 | 77250
|  | 8 |  | Mooring dolphin 5S |  | 3 | hr/pile | 6 | (30-in steel) | day | 0.75 | 61800 | 46350
|  | 9 |  | Mooring dolphin 4S |  | 3 | hr/pile | 6 | (30-in steel) | day | 0.75 | 61800 | 46350
|  | 10 |  | Mooring dolphin 3S |  | 3 | hr/pile | 6 | (30-in steel) | day | 0.75 | 61800 | 46350
|  | 11 |  | Mooring dolphin 2S |  | 3 | hr/pile | 6 | (30-in steel) | day | 0.75 | 61800 | 46350
|  | 12 |  | Mooring dolphin 1S |  | 3 | hr/pile | 10 | (30-in steel) | day | 1.25 | 61800 | 77250
|  | 13 |  | Bresting dolphin 1N |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 14 |  | Bresting dolphin 2N |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 15 |  | Bresting dolphin 3N |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 16 |  | Bresting dolphin 4N |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 17 |  | Bresting dolphin 5N |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 18 |  | Bresting dolphin 6N |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 19 |  | Bresting dolphin 6S |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 20 |  | Bresting dolphin 5S |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 21 |  | Bresting dolphin 4S |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 22 |  | Bresting dolphin 3S |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 23 |  | Bresting dolphin 2S |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 24 |  | Bresting dolphin 1S |  | 4.2 | hr/pile | 4 | (42-in steel) | day | 0.7 | 61800 | 43260
|  | 25 |  | N. unloading platform |  | 5.4 | hr/pile | 23 | (54-in conc) | day | 5.175 | 61800 | 319815
|  | 26 |  | S. unloading platform |  | 5.4 | hr/pile | 23 | (54-in conc) | day | 5.175 | 61800 | 319815
|  | 27 |  | N. service platform |  | 5.4 | hr/pile | 16 | (54-in conc) | day | 3.6 | 61800 | 222480
[11 empty] | Subtotal this sheet: |  | 2107380

## Offshore Dem 11
Exhibit No. DCP-27
Page 24 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
V. | Offshore Demolition Work
C. Phase 3
4. Pile removal
Estimated
|  | a. | Using 100 ton revolving crane or shear leg crane (continued) | [8 empty] | Cost
[9 empty] | Unit | No. | Unit Cost | (2006$)
|  | 28 | S. service platform |  | 5.4 | hr/pile | 16 | (54-in conc) | day | 3.6 | 61800 | 222480
|  | 29 | Operations platform |  | 5.4 | hr/pile | 41 | (54-in conc) | day | 9.225 | 61800 | 570105
|  | 30 | Small craft dock |  | 1.8 | hr/pile | 31 | (18-in steel) | day | 2.325 | 61800 | 143685
|  | 31 | N. access roadway and pipeway |  | 5.4 | hr/pile | 30 | (54-in conc) | day | 6.75 | 61800 | 417150
|  | 32 | S. access roadway and pipeway |  | 5.4 | hr/pile | 30 | (54-in conc) | day | 6.75 | 61800 | 417150
|  | 33 | Center roadway and pipeway |  | 5.4 | hr/pile | 6 | (54-in conc) | day | 1.35 | 61800 | 83430
|  | 34 | Center tee road |  | 5.4 | hr/pile | 9 | (54-in conc) | day | 2.025 | 61800 | 125145
|  | 35 | Walkway supports (MD-1N-MD-2N) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 36 | Support BD-1N walkway (E end) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 37 | Support BD-1N walkway (W end) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 38 | Support BD-4N walkway (E end) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 39 | Support BD-5N walkway (E end) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 40 | Walkway supports (MD-1S & MD-2S) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 41 | Support BD-1S walkway (W end) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 42 | Support BD-1S walkway (E end) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 43 | Support BD-4S walkway (E end) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 44 | Support BD-5S walkway (E end) |  | 3.6 | hr/pile | 2 | (36-in conc) | day | 0.3 | 61800 | 18540
|  | 45 | Demobilization of revolving crane | [5 empty] | day | 2 | 61800 | 123600
[10 empty] | Subtotal (this sheet): |  | 2288145
|  |  |  | Total pile removal using 100 ton revolving crane or shear leg crane: | [7 empty] | 4395525
C. Phase 3
5. Bottom debis check and clearance
|  | a. | Side scan sonar check | [5 empty] | L.S. |  | 15000 | 15000
|  | b. | Debris removal (50 ton barge) | [5 empty] | day | 10 | 42400 | 424000
|  |  |  | Total debris check and clearance: | [7 empty] | 439000

## Salvage
Exhibit No. DCP-27
Page 25 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
VI. Salvage
Estimated
Salvage
| A. Equipment | [7 empty] | (2006$)
|  | 1 | Wastewater recovery unit (101-BA) | [5 empty] | 225
|  | 2 | Wastewater recovery unit (101-BB) | [5 empty] | 225
|  | 3 | Wastewater recovery unit (101-BC) | [5 empty] | 225
|  | 4 | Wastewater recovery unit (101-BD) | [5 empty] | 225
|  | 5 | Boil-off gas heater (102-CA) | [5 empty] | 750
|  | 6 | Boil-off gas heater (102-CB) | [5 empty] | 750
|  | 7 | Fuel gas heater (103-CA) | [5 empty] | 175
|  | 8 | Fuel gas heater (103-CB) | [5 empty] | 175
|  | 9 | Purge gas heater (104-C) | [5 empty] | 175
|  | 10 | Purge gas heater (105-CA) | [5 empty] | 175
|  | 11 | Purge gas heater (105-CB) | [5 empty] | 175
|  | 12 | Purge gas heater (106-CA) | [5 empty] | 175
|  | 13 | Purge gas heater (106-CB) | [5 empty] | 175
|  | 14 | Compressor intercooler (107, 108, 109, 110, 114-CA) | [5 empty] | 350
|  | 15 | Compressor intercooler (107, 108, 109, 110, 114-CB) | [5 empty] | 350
|  | 16 | Compressor intercooler (107, 108, 109, 110, 114-CC) | [5 empty] | 350
|  | 17 | LNG vapor economizer (113-CA) | [5 empty] | 550
|  | 18 | LNG vapor economizer (113-CB) | [5 empty] | 550
|  | 19 | Purge gas heater (115-C) | [5 empty] | 175
|  | 20 | Turbine generator cooling water cooler (116-CA) | [5 empty] | 300
|  | 21 | Turbine generator cooling water cooler (116-CB) | [5 empty] | 300
|  | 22 | Turbine generator cooling water cooler (116-CC) | [5 empty] | 300
|  | 23 | Salt bath heater (117-C) | [5 empty] | 325
|  | 24 | Fire water tank heater (118-C) | [5 empty] | 175
|  | 25 | Emergency generator fuel tank (119-F) | [5 empty] | 110
|  | 26 | Cooling water pump surge tank | [5 empty] | 300
|  | 27 | Fire pump fuel tank (122-F) | [5 empty] | 110
|  | 28 | LNG vaporizer exhaust blower (107-J) | [5 empty] | 650
|  | 29 | Send out booster pumps (10) | [5 empty] | 2500
|  | 30 | Gas turbine generator set (3) | [5 empty] | 7500
|  | 31 | LNG booster pumps (3) | [5 empty] | 750
|  | 32 | Vapor compressor | [5 empty] | 250
|  | 33 | Boil-off compressors (3) | [5 empty] | 31500
|  | 34 | Air compressor | [5 empty] | 175
|  | 35 | Fire pumps (2) | [5 empty] | 500
|  | 36 | Jockey pump | [5 empty] | 100
|  | 37 | Economizer water circulation pump (114-JA) | [5 empty] | 220
|  | 38 | Economizer water circulation pump (114-JB) | [5 empty] | 220
|  | 39 | Economizer water circulation pump (114-JC) | [5 empty] | 220
|  | 40 | LNG liquid pump (115-J) | [5 empty] | 150
|  | 41 | LNG liquid pump (115-JA) | [5 empty] | 150
|  | 42 | Collection pond sump pump (118-JA) | [5 empty] | 110
|  | 43 | Collection pond sump pump (118-JB) | [5 empty] | 110
[7 empty] | Subtotal this sheet: |  | 52975
Exhibit No. DCP-27
Page 26 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
VI. Salvage
Estimated
Salvage
| A. Equipment (continued) | [7 empty] | (2006$)
|  | 44 | Collection pond sump pump (119-JA) | [5 empty] | 110
|  | 45 | Collection pond sump pump (118-JB) | [5 empty] | 110
|  | 46 | Rollover pump (121-JA) | [5 empty] | 110
|  | 47 | Rollover pump (121-JB) | [5 empty] | 110
|  | 48 | Cooling water circulation pump (125-JA) | [5 empty] | 175
|  | 49 | Cooling water circulation pump (125-JB) | [5 empty] | 175
|  | 50 | Cooling water circulation pump (125-JC) | [5 empty] | 175
|  | 51 | Well pump (128-J) | [5 empty] | 360
|  | 52 | Glycol pump (134-J) | [5 empty] | 110
|  | 53 | Propane loading pump (135-J) | [5 empty] | 175
[7 empty] | Subtotal this sheet: |  | 1610
[7 empty] | Subtotal: |  | 54585
|  | 1 | Liquefaction unit |  | (1995 vintage) |  |  |  | 366383
|  | 2 | Air separation unit |  | (2003 vintage) |  |  |  | 366383
[7 empty] | Subtotal: |  | 732766
[6 empty] | Total equipment salvage: |  |  | 787351
| B. Valves | [7 empty] | 23200
[6 empty] | Total valve salvage: |  |  | 23200
C. Material
|  | 1 | Aluminum |  |  |  |  | Unit
|  |  | a. Onshore |  |  | Quantity | Unit | Price | Total
|  |  | 1 | Scrap from LNG storage tank 101 FA |  | 548 | ton | 1200 | 657600
|  |  | 2 | Scrap from LNG storage tank 101 FB |  | 548 | ton | 1200 | 657600
|  |  | 3 | Scrap from LNG storage tank 101 FC |  | 548 | ton | 1200 | 657600
|  |  | 4 | Scrap from LNG storage tank 101 FD |  | 548 | ton | 1200 | 657600
[7 empty] | Subtotal onshore: |  | 2630400
b. Offshore
|  |  | 1 | Stairs, etc. |  | 22 | ton | 1200 | 26400
[7 empty] | Subtotal offshore: |  | 26400
[6 empty] | 1. Total aluminum: |  |  | 2656800
|  | 2 | Carbon steel plate
a. Onshore
|  |  | 1 | Scrap from LNG storage tank 101 FA |  | 1535 | ton | 120 | 184200
|  |  | 2 | Scrap from LNG storage tank 101 FB |  | 1535 | ton | 120 | 184200
|  |  | 3 | Scrap from LNG storage tank 101 FC |  | 1535 | ton | 120 | 184200
|  |  | 4 | Scrap from LNG storage tank 101 FD |  | 1535 | ton | 120 | 184200
[7 empty] | Subtotal this sheet: |  | 736800
Exhibit No. DCP-27
Page 27 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
VI. Salvage
| C. Material (continued) | [6 empty] | Unit
[6 empty] | Quantity | Unit | Price | Total
|  |  | 5 | Scrap from LNG storage tank E |  | 2508.0776 | ton | 120 | 300969.3156
|  |  | 6 | Firewater storage tank 110-FA (80' diameter) |  | 83 | ton | 120 | 9960
|  |  | 7 | Firewater storage tank 110-FB (80' diameter) |  | 83 | ton | 120 | 9960
|  |  | 8 | Fuel gas scrubber (105-F) |  | 1 | ton | 120 | 120
|  |  | 9 | Fuel gas scrubber (106-F) |  | 5 | ton | 120 | 600
|  |  | 10 | Water storage tank (111-F) |  | 6 | ton | 120 | 720
|  |  | 11 | Economizer water storage tank (112-F) |  | 4 | ton | 120 | 480
|  |  | 12 | NG vapor scrubber (114-F) |  | 10 | ton | 120 | 1200
|  |  | 13 | Glycol tank (126-F) |  | 6 | ton | 120 | 720
|  |  | 14 | Propane storage tank (127-F) |  | 15 | ton | 120 | 1800
|  |  | 15 | Vent stack (128-F) |  | 11 | ton | 120 | 1320
|  |  | 16 | Lube oil storage (129-F) |  | 4 | ton | 120 | 480
|  |  | 17 | Lube oil storage tank (130-F) |  | 3 | ton | 120 | 360
|  |  | 18 | Dewar tank (110-L) |  | 26 | ton | 120 | 3120
[7 empty] | Subtotal this sheet: |  | 331809.3156
[7 empty] | Subtotal onshore: |  | 1068609.3156
b. Offshore
|  |  | 1 | Dewar tank (offshore) |  | 26 | ton | 120 | 3120
|  |  | 2 | North and south control towers |  | 14 | ton | 120 | 1680
|  |  | 3 | Misc. structural steel |  | 7 | ton | 120 | 840
[7 empty] | Subtotal offshore: |  | 5640
[6 empty] | 2. Total carbon steel plate: |  |  | 1074249.3156
|  | 3 | Carbon steel pipe
|  |  | a. Onshore steel pipe |  |  | 582 | ton | 120 | 69840
|  |  | b. M&R (2003 vintage) |  |  | 50 | ton | 120 | 6000
|  |  | c. Offshore steel pipe |  |  | 33 | ton | 120 | 3960
[6 empty] | 3. Total carbon steel pipe: |  |  | 79800
|  | 4 | Stainless steel pipe
|  |  | a. Onshore stainless steel pipe |  |  | 592 | ton | 1200 | 710400
|  |  | b. Offshore stainless steel pipe |  |  | 200 | ton | 1200 | 240000
[6 empty] | 4. Total stainless steel pipe: |  |  | 950400
|  | 5 | Stainless steel plate
a. Onshore stainless steel plate
|  |  | 1 | Scrap from LNG storage tank E |  | 2508.0776 | ton | 1200 | 3009693.1557
|  |  | 1 | Booster pump surge tank (104-F) |  | 14 | ton | 1200 | 16800
[7 empty] | Subtotal onshore: |  | 3026493.1557
b. Offshore
|  |  | 1 | Surge tank 102-FA |  | 7 | ton | 1200 | 8400
|  |  | 2 | Surge tank 102-FB |  | 7 | ton | 1200 | 8400
|  |  | 3 | Tank 103-FA |  | 1 | ton | 1200 | 1200
|  |  | 4 | Tank 103-FB |  | 1 | ton | 1200 | 1200
[7 empty] | Subtotal offshore: |  | 19200
[6 empty] | 5. Total stainless steel plate: |  |  | 3045693.1557
Exhibit No. DCP-27
Page 28 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
VI. Salvage
C. Material (continued)
|  | 6 | Structural steel |  |  |  |  | Unit
[6 empty] | Quantity | Unit | Price | Total
|  |  | a. Building 103-H |  |  | 32.5 | ton | 120 | 3900
|  |  | b. Building 104-H |  |  | 92.8 | ton | 120 | 11136
|  |  | c. Building 105-H |  |  | 64.2 | ton | 120 | 7704
|  |  | d. Building 106-H |  |  | 102.8 | ton | 120 | 12336
|  |  | e. Building 107-H |  |  | 54 | ton | 120 | 6480
|  |  | f. Building 110-H |  |  | 13.3 | ton | 120 | 1596
|  |  | g. Warehouse building |  |  | 23 | ton | 120 | 2760
|  |  | h. From pipe supports and sleepers |  |  | 36.2 | ton | 120 | 4344
|  |  | i. Misc. |  |  | 52.6 | ton | 120 | 6312
[6 empty] | 6. Total structural steel: |  |  | 56568
|  | 7 | Elecrical cable
|  |  | a. Insulated electrical cable |  |  | 123000 | lb | 1 | 123000
[6 empty] | 7. Total electrical cable: |  |  | 123000
[6 empty] | Total material salvage: |  |  | 7986510.4713

## LNG Tank Estimate
Exhibit No. DCP-27
Page 29 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
Estimated Cost to Remove Cove Point LNG Tanks
Estimated Cost to Purge, Clean and Dismantle 850,000 Barrel LNG Storage Tank
Estimated
| Cost Element |  |  | Cost
1 | Construction labor |  |  | 2800000
2 | Insulation |  |  | 1600000
3 | Electrical |  |  | 200000
4 | Purge and clean |  |  | 250000
| Total: |  |  | 4850000
Estimated Cost to Purge, Clean, and Dismantle 375,000 Barrel LNG Storage Tanks Using 6/10 Rule
| (a) | (b) | (c) | (d)
Est. Cost to
Purge, Clean,
|  | Tank |  | and Dismantle
| LNG | Volume | 6/10 | LNG Tank
| Tank | (Barrels) | Factor | (2006 $)
1 | E | 850000 | 1 | 4850000
2 | 101-FA | 375000 | 0.61202 | 2968309.2388
3 | 101-FB | 375000 | 0.61202 | 2968309.2388
4 | 101-FC | 375000 | 0.61202 | 2968309.2388
5 | 101-FD | 375000 | 0.61202 | 2968309.2388
16723236.9551

## Workpapers Onshore
Exhibit No. DCP-27
Page 30 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
1 | Cost escalation factor December 1993 to March 2006
See Note (1)
ENR
Construction
|  |  | Time |  | Cost
|  |  | Period |  | Indice
|  | 1 | 1993-12-01 |  | 5310
|  | 2 | 2006-03-01 |  | 7692
|  |  | Escalation factor = |  | 7692/5310 = | 1.4486
|  | Note: | 1 See ENR March 20, 2006
2 | CB&I estimate to remove 850,000 barrel storage tank
Estimated
| Cost Element |  |  | Cost
1 | Engineering & project team |  |  | 960000
2 | Construction labor |  |  | 2800000
3 | Earthen Dikes & MSE Walls |  |  | 1000000
4 | Insulation |  |  | 1600000
5 | Electrical |  |  | 200000
6 | Purge and clean |  |  | 250000
7 | Contingency at 10 percent |  |  | 680000
| Total: |  |  | 7500000 | (rounded)
3 | Calculation of scrap tonage from LNG storage tanks
|  |  |  | Carbon |  | Stainless
| LNG | Tank |  | Steel | Aluminum | Steel
| Tank | Volume | 6/10 Factor | Scrap | Scrap | Scrap
| No. | (Barrels) | Factor | (tons) | (tons) | (tons)
1 | E | 850000 | 1.6339 | 2508.0776 | 0 | 2508.0776
2 | 101-FA | 375000 | 1 | 1535 | 548 | 0
3 | 101-FB | 375000 | 1 | 1535 | 548 | 0
4 | 101-FC | 375000 | 1 | 1535 | 548 | 0
5 | 101-FD | 375000 | 1 | 1535 | 548 | 0
| Total: |  |  | 8648.0776 | 2192 | 2508.0776

## Workpapers Offshore
Exhibit No. DCP-27
Page 31 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
Marine contractor labor rates
Marine contractor labor rates for roustabouts
|  |  |  | Year 2004 |  | March 2006
|  |  |  | Labor Rate |  | Labor Rate
|  |  |  | Including | (Note 1) | Including
|  |  |  | Fringe | Escalation | Fringe
|  |  |  | Benefits | Factor | Benefits
|  | Trade |  | ($/hr) |  | ($/hr)
Operating engineers:
1 |  | Crane operator |  | 70 | 1.08 | 75.6
2 |  | Heavy equipment |  | 65 | 1.08 | 70.2
3 |  | Small equipment |  | 48 | 1.08 | 51.84
4 |  | Pipefitter/welder |  | 80 | 1.08 | 86.4
5 |  | Pipefitter/welder helper |  | 48 | 1.08 | 51.84
6 |  | Teamster |  | 48 | 1.08 | 51.84
7 |  | Laborer |  | 40 | 1.08 | 43.2
8 |  | Foreman |  | 81 | 1.08 | 87.48
Marine equipment rates:
9 |  | flatbed truck |  | 45 | 1.08 | 48.6
10 |  | John Deere 160 LC excavator |  | 120 | 1.08 | 129.6
11 |  | welding rig |  | 20 | 1.08 | 21.6
Note
| 1 | Escalation factor based on ENR construction cost indices for 2004 of 7115 and March 2006 of 7692 per ENR 3/20/06.
A. |  | Equipment removal and pipe cutting spread
|  |  | Labor/Equipment | No. | Hours | Rate | Total
flatbed truck |  |  |  | 1 | 8 | 48.6 | 388.8
hydrocrane, Grove, 15 ton |  |  |  | 1 | 8 | 36.49 | 291.92
welding rig |  |  |  | 1 | 8 | 21.6 | 172.8
operator |  |  |  | 1 | 8 | 75.6 | 604.8
teamster |  |  |  | 1 | 8 | 51.84 | 414.72
pipefitter/welder |  |  |  | 2 | 8 | 138.24 | 2211.84
helper |  |  |  | 2 | 8 | 51.84 | 829.44
foreman |  |  |  | 1 | 8 | 87.48 | 699.84
5614.16
B. |  | Laborer spread
Equipment |  |  |  | No. | Hours | Rate | Total
flatbed truck |  |  |  | 1 | 8 | 48.6 | 388.8
teamster |  |  |  | 1 | 8 | 51.84 | 414.72
laborer |  |  |  | 4 | 8 | 43.2 | 1382.4
foreman |  |  |  | 1 | 8 | 87.48 | 699.84
2885.76
Exhibit No. DCP-27
Page 32 of 32
Dominion Cove Point LNG, LP
Final Abandonment Estimate LNG Terminal
C. |  | Concrete demolition spread
|  |  | Labor/Equipment | No. | Hours | Rate | Total
flatbed truck |  |  |  | 1 | 8 | 48.6 | 388.8
John Deere 160 LC excavator |  |  |  | 1 | 8 | 129.6 | 1036.8
air compressor |  |  |  | 1 | 8 | 22 | 176
operator |  |  |  | 1 | 8 | 75.6 | 604.8
teamster |  |  |  | 1 | 8 | 51.84 | 414.72
laborer |  |  |  | 4 | 8 | 43.2 | 1382.4
foreman |  |  |  | 1 | 8 | 87.48 | 699.84
4703.36
D. |  | Fifty ton revolving crane barge spread
|  |  |  | No. |  | Rate | Total
cargo barge (184x54) |  |  |  | 1 |  | 2000 | 2000
cargo barge (184x54) |  |  |  | 1 |  | 2000 | 2000
50 ton revolving crane barge |  |  |  | 1 |  | 19200 | 19200
tug boat (2000 hp) |  |  |  | 2 |  | 6600 | 13200
utility boat |  |  |  | 1 |  | 6000 | 6000
42400
E. |  | One hundred ton revolving crane barge spread
|  |  |  | No. |  | Rate | Total
cargo barge (250x72) |  |  |  | 2 |  | 4000 | 8000
100 ton revolving crane barge |  |  |  | 1 |  | 24000 | 24000
utility boat |  |  |  | 1 |  | 6000 | 6000
tug boat for cargo barge (2000 hp) |  |  |  | 2 |  | 6600 | 13200
tug boat for crane barge (2000 hp) |  |  |  | 1 |  | 6600 | 6600
diving service |  |  |  | 1 |  | 2000 | 2000
dive boat |  |  |  | 1 |  | 2000 | 2000
61800
F. |  | 250 ton shear leg crane barge spread
|  |  |  | No. |  | Rate | Total
cargo barge (250x72) |  |  |  | 2 |  | 4000 | 8000
250 ton shear leg crane |  |  |  | 1 |  | 24000 | 24000
utility boat |  |  |  | 1 |  | 6000 | 6000
tug boat for cargo barge (2000 hp) |  |  |  | 2 |  | 6600 | 13200
tug boat for crane barge (2000 hp) |  |  |  | 1 |  | 6600 | 6600
diving service |  |  |  | 1 |  | 2000 | 2000
dive boat |  |  |  | 1 |  | 2000 | 2000
61800