MARITIMES & NORTHEAST PIPELINE, L.L.C.

Description of Company Operations

STATEMENT O		Description of Company Operations

STATEMENT O(1)		Detailed System Map

STATEMENT O(2)		Modifications Since Last Rate Proceeding

STATEMENT O(3)		Description of System Design and Operation

## Description of Company Operations

The facilities owned by Maritimes & Northeast Pipeline, L.L.C. (Maritimes-US) consist of the following: 1) a pipeline system wholly owned by Maritimes-US which extends from a point near Woodland, Maine, at the international border between Canada and the United States of America to Westbrook, Maine; 2) a pipeline jointly owned by Maritimes-US and the Portland Natural Gas Transmission System which extends from Westbrook, Maine through the State of New Hampshire to a terminus near Dracut, Massachusetts and 3)a pipeline wholly owned by Maritimes-US which extends from a point near Methuen, Massachusetts to a terminus in the Beverly/Salem, Massachusetts area.

The capacity rights of Maritimes-US on the jointly owned facilities are described in those certain Definitive Agreements approved by the Commission in its order issued on November 4, 1997 in Docket Nos. CP97-238-001 and CP96-178-004.  The FERC gave final approval for the joint facilities in its orders issued on July 31, 1997 and September 24, 1997 in Docket Nos. CP96-178 et. al., CP96-809 et. al. and CP97-238 et. al.  For Maritimes-US wholly owned facilities the FERC gave final approval in its

orders issued on July 31, 1998 and April 14, 1999 in Docket Nos. CP96-178 et. al. and CP96-809 et. al.  Maritimes-US placed a portion of the jointly owned pipeline into service on March 10, 1999 and commenced full operation of the pipeline from the US/Canadian border to Dracut on December 1, 1999.  Maritimes-US placed its Phase III facilities in service on November 24, 2003. The Commission approved these facilities in orders issued on December 21, 2001 and June 4, 2002 in Docket Nos. CP01-4-000 and CP01-4-001.

History of Filings for Major Expansions Subsequent to June, 2002:

Since the filing of its last rate proceeding in Docket No. RP02-134, Maritimes-US has made the following modifications to its system.

- M&N Phase III Extension, added a 30-inch diameter extension to the M&N mainline from a tap on the Joint Facilities at approximate milepost 10.8 extending in a southeasterly direction for approximately 25.13 miles to an interconnection with Algonquin Gas Transmission Company’s (Algonquin) HubLine Project.  The Phase III project included a meter station in Methuen, MA (M&R 30024) at the tap on the Joint Facilities and a second meter station in Salem, MA (M&R 30025) near the interconnection with Algonquin. Phase III was originally filed under Docket No. CP01-4-000 on October 10, 2000 and approved by the Commission’s Order Issuing Certificates dated December 21, 2001. Maritimes subsequently filed an amendment under Docket No. CP01-4-001 on January 23, 2002, as approved by the Commission’s Order Amending Certificates dated June 4, 2002.  The Phase III Project went into service on or about November 24, 2003.

- Added metering facilities in Westbrook, ME (M&R 30026) at approximate mile post 101.5, under its

Blanket Authorization with an in-service date on or about September 30, 2003 to allow reverse flow into Portland Natural Gas Transmission System’s pipeline.

Description of System Design and Operation

The flow formula used for facility design on Maritimes' System is known as the Panhandle A flow equation and it is set forth below.  The Panhandle A flow equation is stated in terms of gas measured in thousands of cubic feet (MCF) at 14.73 psia and 60oF.  Since Maritime's Gas tariff and service agreements specify contract amounts in Dth on a dry basis, a conversion from Mcf to Dth is required.  Gas entering the Maritimes-US System near Woodland, ME uses a conversion factor of 1.043 and is based upon the assumption that an MCF of gas delivered has a heat content of 1,043 BTU/cubic foot.

Gas from Portland Natural Gas Transmission System which, commingles with M&N gas at Westbrook, ME (M&R 30006, approximate Milepost 101.5), uses a conversion factor of 1.000 based on the assumption that an MCF of PNGTS gas has a heat content of 1,000 BTU/cubic foot.

Pipe is sized in accordance with the Panhandle A flow equation which is stated as:

Q=435.87EToPo1.07881P12−P22G0.8539TfL0.5394(D)2.6182

1

Where:

Q =	Rate of Gas flow, cubic feet per day measured at base pressure and temperature conditions Po and To, respectively.

Po =	Pressure base for gas measurement, PSIA

To =	Temperature base for gas measurement, Degrees Fahrenheit absolute

E =	Pipeline segment flow efficiency, decimal fraction

G =	Specific Gravity of Gas, Air = 1.0

P1 =	Pipeline segment inlet pressure, PSIA

P2 =	Pipeline segment outlet pressure, PSIA

Tf =	Mean flowing temperature of gas in pipeline segment, Degrees Fahrenheit absolute

L =	Length of pipeline segment, miles

D =	Inside diameter of pipeline segment, inches

The Mean Flowing Temperature, Tf, was calculated by the following equations:

K=0.4339UoDCpQG

2

Where:

Tf=Tg+Ti−TgKL1−1eKL

3

Tf =	Mean Flowing Temperature, Degrees Fahrenheit

Ti = Pipeline segment initial temperature, Degrees Fahrenheit

Tg = Pipeline segment ground temperature, Degrees Fahrenheit

L =	Previously defined

Uo =	Overall heat transfer coefficient, BTU/Hr-ft2-degrees F

D =	Outside diameter of pipeline segment, inches

Cp =	Specific heat of gas in pipeline segment at constant Pressure, BTU/lb - degree F

Q =	Rate of gas flow, million cubic feet per day measured at 14.73 psia and 60 degrees F

G =	Previously defined

E =	2.71828, base of the Naperian logarithms

The design parameters used in the above gas flow equations are as follows:

E = 				0.93

Po =				14.73 PSIA

Ti =				60 Degrees Fahrenheit

Tg =				50 Degrees Fahrenheit

G = Spec Gravity	0.61 (Air = 1.0)

Uo =				0.50

Cp =				0.5117

The following equation was used to determine the horsepower required at the individual compressor stations:

Where:

Hp=QMZTE

Hp =	Horsepower required

Q =	Volume throughput, million cubic feet per day measured at 14.73 psia and 60 degrees Fahrenheit.

E =	Compressor Efficiency

Z =	Gas compressibility factor from P&RG-15

T = 	Suction temperature correction factor from P&RG-143 or P&RG-351

M =	Hp to compress one million cubic feet per day

For centrifugal compressors taken from P&RG-351

For reciprocating compressors, taken from P&RG-143

Valve and piping losses at each compressor station are assumed to be 5 psi on the suction side and 9 psi on the discharge side.  The discharge side losses include a 4 psi allowance for losses through the cooling bays at each station.

In accordance with 18 C.F.R. § 157.14(a)(9)(vi), Maritimes hereby certifies that it will design, install, inspect, test, construct, operate, replace, and maintain the facilities in accordance with Federal safety standards and plans for maintenance and inspection.

81 FERC ¶ 61,166 (1997)

80 FERC ¶ 61,136 (1997)

80 FERC ¶ 61,345 (1997)

84 FERC ¶ 61,130 (1998)

87 FERC ¶ 61,061 (1999)

97 FERC ¶ 61,345 (2001)

99 FERC ¶ 61,277 (2002)

97 FERC ¶ 61,345 (2001)

99 FERC ¶ 61,277 (2002)

Subpart F Blanket Cert. July 31, 1997 (80 FERC ¶ 61,136 (1997))