MARITIMES & NORTHEAST PIPELINE, L.L.C.

Description of Company Operations

STATEMENT O		Description of Company Operations

STATEMENT O(1)		Detailed System Map

STATEMENT O(2)		Modifications Since Last Rate Proceeding

STATEMENT O(3)		Description of System Design and Operation

## Description of Company Operations

The facilities owned by Maritimes & Northeast Pipeline, L.L.C. (“Maritimes”) consist of the following: 1) a pipeline system wholly owned by Maritimes which extends from two interconnections near Baileyville, Maine at the U.S.–Canada international border, one with Maritimes’ Canadian pipeline affiliate, Maritimes & Northeast Pipeline Limited Partnership, and a second with Emera Brunswick Pipeline Company Ltd. (“Brunswick Pipeline”) to Westbrook, Maine; 2) a pipeline jointly owned by Maritimes and Portland Natural Gas Transmission System (“PNGTS”) which extends from Westbrook, Maine through the State of New Hampshire to a terminus at an interconnection with Tennessee Gas Pipeline Company near Dracut, Massachusetts; 3) a pipeline wholly owned by Maritimes which extends from a point near Methuen, Massachusetts, to a terminus at an interconnection with Algonquin Gas Transmission, LLC in the Beverly, Massachusetts area (“Phase III”); 4) facilities consisting of the following laterals jointly owned by Maritimes and PNGTS: the Newington Lateral, the Westbrook Lateral and the Haverhill Lateral; and (5) facilities consisting of the following laterals wholly owned by Maritimes: the Bucksport Lateral and the Veazie Lateral.

With respect to Maritimes’ wholly-owned facilities, the Commission issued a certificate of public convenience and necessity in its orders issued on July 31, 1998, and April 14, 1999, in Docket Nos. CP96-178, et. al. The Commission issued a certificate of public convenience and necessity for the jointly-owned facilities (“Joint Facilities”) in its orders issued on July 31, 1997, and September 24, 1997, in Docket Nos. CP97-238, et. al.  Maritimes placed a portion of its interest in the Joint Facilities into service on March 10, 1999, and the remainder of its interest in the Joint Facilities, as well as its wholly-owned facilities, with the exception of Phase III, into service on December 1, 1999. The Commission granted a certificate of public convenience and necessity for the Phase III facilities in orders issued on December 21, 2001, and June 4, 2002, in Docket Nos. CP01-4, et. al. Maritimes placed the Phase III facilities into service on November 24, 2003. The Commission granted a certificate of public convenience and necessity for the Phase IV facilities in an order issued on February 21, 2007, in Docket Nos. CP06-335, et. al. Maritimes placed the Phase IV facilities into service on January 15, 2009.

Modifications Since Last Rate Proceeding

Since the filing of its last rate proceeding in Docket No. RP04-360, Maritimes has made the following modifications to its system.

The Haverhill Lateral/ KeySpan Meter Project was filed in Docket No. CP05-74-000 on February 22, 2005, and approved by the Commission on July 27, 2005. The Haverhill Lateral/ KeySpan Meter Project was placed into service on November 1, 2006, and modified the Maritimes system as follows:

- Maritimes constructed a meter station and related interconnect facilities (including approximately 280 feet of 6-inch interconnecting pipe, data equipment, a boiler, a building for the boiler, battery back-up, piping, a tap valve) at a point interconnecting with National Grid’s Essex County Gas Company distribution facilities near Haverhill, Massachusetts;

- Maritimes exchanged 40% of its ownership interest in the Newington Energy Meter Station and related interconnect facilities with PNGTS for the ownership interest necessary to increase Maritimes’ overall ownership interest in the Haverhill Lateral to 22.14% and the existing meter station and interconnect facilities located on the Haverhill Lateral previously owned entirely by PNGTS; and

- Maritimes recorded the abandonment of its 40% ownership interest in the Newington Energy Interconnect facilities on its 2007 Annual Blanket Certificate Report filed on May 1, 2007.

The Phase IV Project was filed in Docket No. CP06-335 on May 16, 2006. Maritimes subsequently filed an amendment to its May 16 application on September 11, 2006. The Phase IV Project was approved by the Commission’s “Order Issuing Certificate and Amending Presidential Permit,” on February 11, 2007. The Phase IV Project was placed into service on January 15, 2009, and added the following facilities to the Maritimes system:

- approximately 1.7 miles of 30-inch diameter pipeline adjacent to the existing 30-inch diameter mainline extending from the St. Croix River crossing   (Mile Post (“MP”) 306.7) at the U.S.-Canadian border to the Baileyville, Maine compressor station (MP 305.0);

- five new compressor stations with a total of approximately 89,881 horse power (hp) including new 18,085 hp compressor stations at Woodchopping Ridge, Maine, Brewer, Maine, and Searsmont, Maine, respectively, two new 13,333 hp compressor units at Westbrook, Maine, and a 8,960 hp compressor unit at Eliot, Maine located on the Joint Facilities;

- modifications to the Dracut Meter Station;

- one new meter station at the Westbrook Compressor Station which replaced Maritimes’ portion of the existing Westbrook inlet meter station where the Joint Facilities mainline and Maritimes’ wholly-owned facilities currently connect;

- one new meter station and odorization facilities at Baileyville, Maine to accommodate receipts of natural gas from the Brunswick Pipeline; and

- modifications to the Baileyville Compressor Station and the Richmond Compressor Station consisting of re-piping the stations so that their units operate in parallel (rather than the previous series) configuration, as well as adding cooling at the Richmond Compressor Station.

Changes to the Definitive Agreements

The capacity rights of Maritimes on the Joint Facilities are described in those certain Definitive Agreements approved by the Commission in its order issued on November 4, 1997, in Docket Nos. CP97-238-001 and CP96-178-004. Amendments to Exhibits A, B and C of the Ownership Agreement became effective as of  January 15, 2009, the date on which Maritimes placed the Phase IV facilities into service. These Exhibits reflect capacity and ownership percentage changes that became effective following the in-service date of the Phase IV facilities.

Description of System Design and Operation

The flow formula used for Maritimes’ system design is known as the “General Flow Equation” and is used in conjunction with the Colebrook-White friction factor. The flow equation is stated in terms of gas measured in units of one-thousand cubic feet (“Mcf”) at 14.73 psia and 60oF.  Since Maritimes’ FERC Gas Tariff and service agreements specify contract amounts in Dekatherms (“Dth”) on a dry basis, a conversion from Mcf to Dth is required.  For gas entering the Maritimes system at Baileyville, Maine, Maritimes uses a conversion factor of 1.043. It is based upon the assumption that an Mcf of gas received has a heat content of 1,043 BTU/cubic foot. The specific gravity for gas received at Baileyville, Maine, is assumed to be 0.577 and to have a temperature of 50 degrees Fahrenheit.  For gas entering the Maritimes system from PNGTS, which commingles with Maritimes’ gas at Westbrook, Maine, Maritimes uses a conversion factor of 1.004. The conversion is based upon the assumption that an Mcf of gas received from PNGTS has a heat content of 1,004 BTU/cubic foot. The specific gravity for gas received from PNGTS is assumed to be 0.580 and to have a temperature of 50 degrees Fahrenheit.

Pipe is sized in accordance with the 
General Flow Equation:

in conjunction with the Colebrook-White friction factor formula:

The variables are defined as follows:

Di =	Inside diameter of pipeline segment, inches

Ep =	Pipeline segment flow efficiency, decimal fraction=1.0

=  	Colebrook-White Friction Factor

G =	Gas Specific Gravity = 0.582 (Air = 1.0)

Ke = 	Pipe Effective Roughness

Internally Coated Pipe = 250 microinches

Bare Steel Pipe        = 750 microinches

L =	Length of pipeline segment, miles

Nre = 	Reynolds Number, dimensionless

P1 =	Pipeline segment inlet pressure, psia

P2 =	Pipeline segment outlet pressure, psia

Pb =	Pressure base for gas measurement, 14.73 psia

Q =	Rate of Gas flow, cubic feet per day measured at base pressure (Pb) and temperature (Tb) conditions.

T =	Gas temperature, oRankin

Tb =	Temperature base for gas measurement, 520o Rankin

Z = 	Compressibility Factor, dimensionless

Ground temperature is set at 55 degrees Fahrenheit for the summer design conditions and 45 degrees Fahrenheit for the winter design conditions.

The required compressor horsepower is calculated using the centrifugal horsepower isentropic equation with allowances for valve and piping losses. Compressor efficiency is assumed to be 0.84. Valve and piping losses at each compressor station are assumed to be 5 psi on the suction side and 5 psi on the discharge side.  Where cooling is present, an additional 4 psi loss is included to account for flow through the gas cooling bays.  Gas cooler discharge temperatures are set at a maximum of 110 degrees Fahrenheit for summer design and 90 degrees Fahrenheit for winter design.

System Operation

Maritimes historically has received gas from Maritimes & Northeast Pipeline Limited Partnership at the Baileyville Meter Station No. 30012.  With the addition of the Phase IV facilities, Maritimes can now receive gas from the Brunswick Pipeline at new Receipt Point No. 30029 located in the immediate vicinity of the Baileyville Meter Station No. 30012.  Typically, gas flows south through the mainline and the Baileyville and Woodchopping Ridge Compressor Stations.  Subject to scheduled nominations, deliveries can be made to the Casco Bay Veazie and Bangor Gas Veazie meters in Veazie, Maine.  As gas flows through the Brewer Compressor Station, deliveries can be made to the Bangor Gas-Orrington Meter Station in accordance with scheduled nominations.  As gas proceeds south through the Searsmont and Richmond Compressor Stations, scheduled deliveries can be made to the Maine Natural-Bowdoin and Northeast Utilities-Lewiston Meter Stations before the gas enters the Westbrook Metering and Compressor Stations and the Joint Facilities. The Joint Facilities also receive and transport gas from PNGTS for redelivery to various points along the Joint Facilities. Scheduled deliveries can be made to the Granite State (“GS”) Westbrook Meter Station and the Maine Natural Gorham Meter Station before entering the Eliot Compressor Station.  South of the Eliot Compressor Station, scheduled deliveries can be made to the GS-Eliot, Newington Energy, Georgia Pacific Gypsum, GS-Newington, Public Service of New Hampshire-Newington, Tennessee Gas-Haverhill and National Grid-Haverhill Meter Stations. The gas flow path then splits, allowing scheduled deliveries to be made into Maritimes’ wholly-owned Phase III facilities that lead to the Beverly interconnection with Algonquin Gas Transmission, LLC. Gas not flowing to Beverly can continue flowing on the Joint Facilities for delivery to the Dracut Meter Station which is at the interconnection with Tennessee Gas Pipeline Company.

84 FERC ¶ 61,130 (1998)

87 FERC ¶ 61,061 (1999)

80 FERC ¶ 61,136 (1997)

80 FERC ¶ 61,345 (1997)

97 FERC ¶ 61,345 (2001)

99 FERC ¶ 61,277 (2002)

118 FERC ¶ 61,137 (2007)

118 FERC ¶ 61,137 (2007)

One unit is located on the Joint Facilities and one is located on Maritimes’ wholly-owned facilities.

10 81 FERC ¶ 61,166 (1997)