HOURLY ARCHIVAL OF SYSTEM LAMBDA

Hourly archival of system LAMBDA reported in the attached file is an hourly integration of

the  value calculated by the Economic Dispatch routine of the Chugach SCADA/EMS system.

System LAMBDA is calculated each time Economic Dispatch is run (approximately every 5

minutes, or triggered by events such as changing units available for Economic Dispatch).  The

following is a description of the Chugach Economic Dispatch System:

ECONOMIC DISPATCH CALCULATION (EDC)

Economic Dispatch Calculation (EDC) is a subroutine of  AGC

which  dispatches  the  system  generation  required to supply a

given load using a simple iterative procedure.  The dispatch  is

based  on the principle of operating all dispatchable generators

at the same incremental cost of generation, or,  system  lambda.

Incremental  transmission losses are considered only in the form

of manually entered penalty factors.  The output of EDC is  used

by AGC to control units.

The Economic Dispatch Calculation (EDC) routine  calculates

the   optimum   economic   megawatt   basepoints   and  economic

participation factors for those generating units under  economic

dispatch.   The  following sections describe in detail the other

features of this routine.   It  should  be  noted  that  EDC  is

structured on the basis of individual generating units.

6.1  EDC FEATURES

Significant features of  the  EDC  routine  are  summarized

below:

1.  The system operator is able to  place  the  EDC  in  an

"evaluation-pass"  mode  of operation by enabling EPME.

The results of the evaluation  pass  dispatch  are  not

passed  to  AGC  but  are  merely made available to the

dispatcher.  This allows determination of the  economic

base  point for generator units that are in manual mode

or in a base loaded mode of operation.

2.  Each  generator  unit  can  be  represented  by   seven

operator-selectable sets of parameters.  Each parameter

set contains:  incremental heat rate curve,  fuel  cost

and incremental maintenance cost.  These allow the user

to build parameter sets with  both  unique  and  common

data to the various sets.

3.  Economic participation factors are  computed  for  both

upward  and  downward  changes  about  the  system load

determined in the  calculation  of  the  economic  base

points   of   the  on-line  EDC.   Note  that  "upward"

participation factors are used when the load  is  above

the  sum  of  the base points, and "downward" ones when

the load is below.

Four dispatches are made during the execution of  the  EDC.

During  calculation  of the unit base points only those units in

FULL mode are dispatched.  Similarly, during the dispatches  for

calculation of economic participation factors only units in FULL

mode are dispatched.  The fourth  dispatch  is  the  "evaluation

pass",  during  which all units which are on line and which have

the  EDC  evaluation  pass  mode  (EPM)  flag,  UEPF,  set   are

dispatched.  If an off-line unit has its EPM flag set, that unit

will be ignored.  If the evaluation  pass  flag,  EPME,  is  not

enabled the evaluation pass dispatch will not be performed.

The following constraints will be respected by EDC  in  all

four dispatch calculations:

1.  Summation of desired  basepoints  at  the  end  of  the

dispatch  will equal the summation of actual generation

of dispatchable units at the beginning of the dispatch,

plus  the  difference  between  the old base points and

current generation for units on base load or base  load

and regulating control, plus filtered ACE (FACE).

2.  High and low economic limits.

3.  Calculated base points will not  violate  the  response

rate limit of the dispatched units.

4.  Units operating outside economic limits will have their

base  points  calculated so as to move the units within

(or towards) economic limits.

EDC will not respect any form of spinning  reserves  rules.

Therefore,  reserves  constraints are not considered as input or

in computations.  In the  event  reserves  are  inadequate,  the

operator   will   be   required   to   take  appropriate  action

independently of EDC.

6.2  METHOD OF CALCULATION

The coordination equations to be solved by EDC are:

(Cj * dfj/dpj + IMj) * PFj = LAMBDA

Where:  Cj       = Fuel cost for the jth unit.

dfj/dpj = Incremental heat rate for the jth unit.

IMj     = Incremental maintenance cost for the

jth unit.

PFj     = Penalty Factor for the jth unit.

Used to bias entire unit cost.

LAMBDA  = Incremental cost of supplying power to a

hypothetical load center of the area.

In addition to the coordination  equations,  the  following

power balance equation must be satisfied:

SUM OF  Basepoints of                    Actual generation of

dispatched           = SUM OF    dispatched units

generation                       (at beginning of

(at end of dispatch)             dispatch)

rate-limited difference

+ SUM OF    between base points and

current generation of

units on ramp, base

load, or base load and

regulating

+ DG

Where:  DG is normally FACE, but is limited to the maximum

MW all units on control may move during the

interval between EDC executions.  DG always has

the same sign as FACE.

The EDC routine consists of an inner and  the  outer  loop.

The  inner  loop  is  a  binary  search  routine for solving the

coordination equations in order to  obtain  base  points  for  a

fixed value of LAMBDA.

During  this  solution  it  is  necessary,  of  course,  to

recognize  the  high  and low economic limits and the calculated

high and low rate  limits.   Once  the  base  points  have  been

determined an outer loop calculation is made to see if the power

balance equation is satisfied.  If not, LAMBDA is adjusted,  the

inner  loop  is  then  reentered  and  a  new set of base points

calculated.

This procedure will continue until one of these  conditions

is met:

1.  Both the coordination equations and the  power  balance

equation are satisfied to within specified tolerances

2.  Either the coordination equations or the power  balance

equation  does  not  converge  because  of numerical or

physical problems.  In this case a message is  sent  to

the system console.

Assuming that a valid solution is  obtained,  the  economic

participation  factors are computed for those units which are to

follow load.  The base points and economic participation factors

(for  the  load following units) are then updated for use by the

AGC routines.  The economic participation factors for the  units

which are not load following are set to zero.

Economic participation factors are calculated  by  assuming

that the slope of the LAMBDA versus generation curve is constant

over a short range.  The load  is  increased  by  a  percentage,

DELEDC,  and  a  new  dispatch  is made.  Economic participation

factors  for  load  above  the  sum  of  base  points  are  then

calculated:

UEPFUPj = (change in unitj generation)/

(change in system load)

The load is then decreased to the same percentage below its

original   value,   and   a  new  dispatch  is  made.   Economic

participation factors for load below the sum of base points  are

calculated in the same way as the increasing ones.

EDC utilizes the Auto-Ranging  Binary  Search  method.   It

operates  by dividing the search region into two, deciding which

half the desired result is in, dividing that half into two,  and

so  on  until a solution is obtained.  Starting with the desired

generation DESGEN (= sum of  all  generation  from  telemetry  +

FACE) and an initial value of LAMBDA (usually the value from the

last EDC), the calculation proceeds until the error (MWn-DESGEN)

is  less  than a set fraction of DESGEN.  This fraction, ERRTPW,

resides in the data base.

The binary  search  algorithm  will  always  work  for  the

Economic  Dispatch  Calculation  when  given  a realistic set of

conditions.  Discontinuous heat rate curve are  also  supported.

Discontinuous  curves  have  slopes that are infinite at certain

points.

6.3  EDC ROUTINES

The main EDC  subroutine  establishes  appropriate  initial

conditions  and  calls the EDC iteration routine (EDCALC):  once

for the  EDC,  (to  establish  base  points  for  the  units  on

control),  once  for  the  evaluation  pass  EDC  (to  establish

recommended generation  for  selected  units),  and  twice  more

during  determination  of  participation  factors.  EDCALC calls

EDDISP once during  each  LAMBDA  iteration  to  determine  unit

generations at the current value of LAMBDA.

6.3.1  Subroutine EDCALC

To dispatch  the  generation,  EDCALC  assumes  an  initial

system  LAMBDA,  computes  the  total  generation when all units

operate at that incremental cost, and compares the  result  with

the  required  generation.   If the difference is greater than a

tolerance value, ERRTPW, LAMBDA is modified, and  the  procedure

is  repeated.   This  sequence  continues  until  the difference

between required and computed total generation falls within  the

tolerance value.

EDCALC is organized into two phases,  the  first  of  which

initializes  several control variables, and determines the upper

and lower bounds for the value of LAMBDA.

The search range  for  LAMBDA  is  determined  as  follows.

Using  the  initial  value  of  LAMBDA  the  total generation is

calculated.  This is either higher or  lower  than  the  desired

value.   The value of this error is multiplied by an estimate of

the slope of the curve to give a LAMBDA step  size.   LAMBDA  is

then  increased  or  decreased  by  the  step size, depending on

whether the error is negative or positive, and total  generation

is   calculated.    When   the   difference  between  calculated

generation and desired generation changes sign the search  range

has been defined.

Now the  binary  search  proper  starts.   The  new  LAMBDA

estimate  is at the center of the range and the step size is set

to 1/4 of the range.  Generation is calculated at this value  of

LAMBDA  and  compared  with  desired generation.  The difference

must be within the tolerance for a converged solution.   If  the

solution  has  not converged, a new LAMBDA estimate is formed by

adding or subtracting the step  size  to  LAMBDA,  depending  on

whether  the  error  is  negative or positive.  The step size is

divided by two and the total generation  at  the  new  operating

point is computed.

This procedure is repeated until the solution converges  or

until  the iteration limit is reached.  If the solution fails to

converge, EDCALC sets a flag to  indicate  convergence  failure.

The last step performed by EDCALC is to determine whether or not

all of the generators on control are at limits,  and  to  set  a

flag if they are all at high limits, or all at low limits.

6.3.2  Subroutine EDDISP

Subroutine EDDISP determines the  power  generated  by  all

units when each unit operates at incremental cost LAMBDA.  Using

the  fuel  cost  for  the  unit,  EDDISP  converts  the   system

incremental  cost to a unit incremental heat rate for each unit.

It uses  this  value  to  locate  the  operating  point  on  the

incremental heat rate curve by interpolation.  If this heat rate

is at a load outside the  unit  economic  limits,  the  unit  is

constrained to the violated limit.

Provision has  been  made  for  the  correct  treatment  of

discontinuous  curves.   The system incremental cost may fall in

the gap between two curve segments;  in this case,  unit  output

is  held  at  that MW value until LAMBDA reaches the upper curve

segment.

6.4  COST DATA

Up to seven economic data sets for each generating unit can

be  defined.   Part of each data set is an incremental heat rate

curve.  These curves consist of 6 straight line segments  (i.e.,

7  points).   The  six straight line segments must at all points

have finite  positive  (non-zero)  slopes,  with  the  following

exception:   discontinuous  curves  may be represented by giving

two heat rate values for a given amount of generation.

For example:

HEATMW   20    40    60    80    100    120    150

HEATR  8500  8750  9250  9500  10000  10250  10500

HEATRP   --  9000     0  9750      0      0     --

Note:  HEATRP unequal to 0 indicates a pair  of  incremental

heat rate points exist for the value of HEATMW.  A 0 for

HEATRP indicates that a pair of points do not exist  for

the  value  of  HEATMW.  A "--" indicates that a pair of

points do not exist for the value of HEATMW (i.e., it is

either  the  first or last point on the incremental heat

rate curve).  The requirement of finite positive  slopes

now applies to each segment individually.

A fuel cost and incremental maintenance cost  are  provided

with each cost curve.