CHAPTER 1

INTRODUCTION

1.1  PURPOSE

The purpose of this document is to describe the algorithms and procedures used to perform the enhanced economic dispatch calculation to operate in accordance with the actual gas contracts. The algorithms and data residency are presented so that they may be reviewed to be sure that they meet Chugach's requirements.

1.2  OVERVIEW

The economic dispatch enhancements are implemented to use the actual gas contracts in force at Beluga to dispatch the generation for Chugach load and economy sales based on multiple gas sources. A two tiered dispatch is used to allow for differing prices for gas used to generate power to meet Chugach's load and power for economy sales. The software does not control or monitor the gas consumed to see whether the distribution of gas between the various sources matches the expectations of the algorithm.

CHAPTER 2

DESCRIPTION

2.1  Implementation

The new Economic Dispatch uses the existing algorithm as described in the EMS Reference Manual, to perform the basic dispatch. However, the overall economic dispatch is now performed in two passes. These two passes are designated primary dispatch and secondary dispatch. The sequence of calculation is given below:

Primary Dispatch

- Set load to Chugach native load. Use actual unit limits and

the primary fuel price.

- Dispatch the generation to meet the load

Secondary Dispatch

- Set load to actual load, including the economy sales. Set the low limits to the primary dispatch unit outputs. Use the Secondary fuel price.

- Dispatch the generation to meet the load

  - Input Data

The following SCADA data quantities will be made available to Economic Dispatch. They are in addition to other data collected

for AGC or Economic Dispatch. Each item is assumed to be available as a single data base item. Where the data is not available, it must be calculated and placed in a computed numeric data base point by some other program.

DESCRIPTION

- CEA native load.

- Economy sales.

- Right of first refusal flag. If set this flag indicates    that Level 6 gas comes from Marathon rather than supplemental gas supplies.

- Unit dedicated to economy sales only flag. (One flag per

unit)

- Basic gas price

- Marathon (Economy Sales) gas price

- Supplemental gas price

- Flag to select allocation algorithm.  0 = Distribute over

the day based on the gas distribution (load profile) curve.

1 = Use the full allocation for the day at each level before

progressing to the next level.

The following constants are defined for Economic Dispatch:

Table of 24 hourly gas distribution values. These might provide a load profile curve or they might be biased to force gas consumption earlier in the day to ensure full utilization of less expensive gas. These values are normalized before use, so any values which express the relative hourly distribution are acceptable.  Default values for these constants would be

provided by load forecasting software.

  - Output Data

These data items are added to the EMS database:

BGC - Basic Gas Consumption. A running accumulation of Basic gas burned at Beluga for Chugach native load. Current accumulation and last hour's accumulation for collection by history.

MGC - Marathon gas consumption. A running accumulation of Marathon gas burned at Beluga for Chugach native load. Current accumulation and last hour's accumulation for collection by history.

SGC - Supplemental gas consumption. A running accumulation of

supplemental gas burned at Beluga for Chugach native load. Current

accumulation and last hour's accumulation for collection by history.

EGC - Economy gas consumption. A running accumulation of gas burned at Beluga for economy sales. Current accumulation and last hour's accumulation for collection by history. This data is stored as a total and on a per unit basis.

GATIME - Time of last gas allocation to provide a means of interpolating gas consumption after a failover.

2.4  Gas Allocation Algorithms

The gas allocation algorithms are based on the description in the letter from Henri Dale to Paul Johnson of October 17, 1990. This is referred to as the Basic method. A variation on the Basic method is the Distributed method. The algorithm in use at any time is dispatcher selectable.

To implement the two pass economic dispatch algorithm two gas prices must be selected. In all cases the secondary dispatch, that is the one which includes economy sales, uses the Marathon gas price. The primary dispatch, the dispatch of Chugach native load, uses different prices based on gas consumption. The two algorithms described below are used to select the gas price to use for the economic dispatch.

2.4.1  The Basic Method

The Basic method ensures that the cheapest gas is always dispatched before the higher priced gas. Within a day, all of the less expensive gas is consumed, followed by the higher priced gas allocations. This means that a given load in the morning might be dispatched using Basic gas, while the same load in the evening might be dispatched using Marathon gas.

The gas price selection is based on the various gas consumption accumulators described above. The numeric limits are expressed in MCF per day.

Level 1 - BGC _<= 45 - Use Basic gas

Level 2 - BGC > 45 and (BGC+MGC+EGC) _<= 55 - Use Marathon gas

Level 3 - (BGC+MGC+EGC) > 55 and BGC _<= 60 - Use Basic gas

Level 4 - BGC > 60 and (BGC+MGC) _<= 70 - Use Marathon gas

Level 5 - 70 _< (BGC+MGC) _<= 80 - Use Supplemental gas

Level 6 - (BGC+MGC) > 80 and RFR = 0 - Use Supplemental gas

(BGC+MGC) > 80 and RFR = 1 - Use Marathon gas

2.4.2  The Distributed Method

The Distributed algorithm attempts to follow the same

gas distribution as the Basic method. However, the various allocations are spread over the entire day so that similar loads are dispatched similarly, regardless of time of day. The risk inherent in this approach is that less expensive gas could remain

undispatched at the end of the day as a result of major shifts in sales or generation at other units.

The gas selection is made using the same levels used by the basic method,except that each numeric threshold is multiplied by a factor, called DD, which represents the portion of the day's load which has passed. DD is calculated based on the gas distribution curve and the time of day. For example, at 10:35 in the morning, assuming the gas distribution curve is flat, DD would be 0.441. The first dispatch in the morning, before any gas has been dispatched, is done using the same level as the previous night.

The main difference between this and the Basic method is in the allocation of gas to the four different categories.

Before the level is selected the Chugach native load gas accumulators (BGC, MGC and SGC) are updated based on the table below. The Native load gas (NGC)gas from the previous

dispatch multiplied by the time that dispatch was in effect (TE) in fraction of a day, is distributed through all levels lower than the current level with the remainder allocated to the accumulator for the current level.

Level = 1 - BGC = BGC+NGC

Level > 1 - BGC = BGC+45*TE

Level = 2 - MGC = MGC+Unallocated NGC

Level > 2 - MGC = MGC+10*TE-Current EGC

Level = 3 - BGC = BGC+Unallocated NGC

Level > 3 - BGC = BGC+15*TE

Level = 4 - MGC = MGC+Unallocated NGC

Level > 4 - MGC = MGC+Current EGC

Level = 5 - SGC = SGC+Unallocated NGC

Level > 5 - SGC = SGC+10*TE

Level = 6 (RFR=0) - SGC = SGC+Unallocated NGC

Level = 6 (RFR=1) - MGC = MGC+Unallocated NGC

CHUGACH ELECTRIC ASSOCIATION, INC.

ANCHORAGE, AK

ECONOMIC DISPATCH WITH MULTIPLE FUEL PRICES

- FUNCTIONAL DESCRIPTION

The proposed Economic Dispatch software enhancement is designed to provide the capability for Chugach to economically dispatch their generation subject to these additional constraints:

When gas flow at Beluga exceeds a specified amount, all additional gas is provided at a different price from the base load gas.

Dispatch power for incremental sales to GVEA on top of Chugach generation at a different price from the Chugach fuel price.

- IMPLEMENTATION

The new Economic Dispatch uses the existing algorithm, as described in the attached appendix, to perform the basic dispatch.  However, the overall economic dispatch is now performed in three passes.  These three passes are designated Base dispatch, Secondary dispatch and GVEA dispatch.  The sequence of calculation is given below:

## Base Dispatch

- Set load to actual load less the GVEA load.  Use actual unit limits and the base fuel price.

- Dispatch the generation to meet the load.

# Secondary Dispatch

If Beluga gas exceeds the base gas consumption limit:

- Dispatch to the base gas limit

- Set the low limits to the dispatched unit outputs.  Use the secondary fuel prices.

- Dispatch the generation to meet the load.

# GVEA DISPATCH

- Set load to actual load, including the GVEA load.  Set the low limits to the dispatched unit outputs.  Use the GVEA fuel prices.

- Dispatch the generation to meet the load.

- PRICE AND DELIVERY

The new Economic Dispatch will be delivered as new or replacement subroutines to be included in the existing AGC program.  Chugach engineers will install and verify the software.

The price for the Economic Dispatch Enhancements described here is $14,400 for work performed prior to September 15, 1990 and an estimated $15,600 for work to be performed after September 15, 1990, charged at a rate of $80.00 per hour.  Total price will not exceed $30,000.00.

APPENDIX A

### METHOD OF CALCULATION

The coordination equations to be solved by EDC are:

(CJ * df/dpj + Imj) * PFj = LAMBDA

Where:  Cj	     = Fuel cost for the jth unit.

dfj/dpj         = Incremental heat rate for the jth unit.

IMj               = Incremental maintenance cost for the jth unit.

PFj               = Penalty Factor for the jth unit.

Used to bias entire unit cost.

LAMBDA     = Incremental cost of supplying power to a hypothetical load center of the

area.

In addition to the coordination equations, the following power balance equation must be satisfied:

SUM OF    Basepoints of

dispatched                        =  SUM OF                    Actual generation of dispatched

generation                                                                units (at beginning of dispatch)

(at end of dispatch)

+ SUM OF                     rate-limited difference between

base points and current generation

of units on ramp, base load, or base

load and regulating

+ DG

Where: DG is normally FACE, but is limited to the maximum MW all units on control may move

during the interval between EDC executions.  DG always has the same sign as FACE.

The EDC routine consists of an inner and outer loop.  The inner loop is a binary search routine for solving the coordination equations in order to obtain base points for a fixed value of LAMBDA.

During this solution it is necessary, of course, to recognize the high and low economic limits and the calculated high and low rate limits.  Once the base points have been determined an outer loop calculation is made to see if the power balance equation is satisfied.  If not, LAMBDA is adjusted, the inner loop is then reentered and a new set of base points calculated.

This procedure will continue until one of these conditions is met:

- Both the coordination equations and the power balance equation are satisfied to within

specified tolerances.

2.     Either the coordination equations or the power balance equation does not converse because of

numerical or physical problems.  In this case a message is sent to the system console.

Assuming that a valid solution is obtained, the economic participation factors are computed for those units, which are to follow load.  The base points and economic participation factors (for the load following units) are then updated for use by the AGC routines.  The economic participation factors for the units which are not load following are set to zero.

Economic participation factors are calculated by assuming that the slope of the LAMBDA versus generation curve is constant over a short range.  The load is increased by a percentage, DELEDC, and a new dispatch is made.  Economic participation factors for load above the sum of base points are then calculated:

UEPFUPj   =   (change in unitj generation)/

(change in system load)

The load is then decreased to the same percentage below its original value, and a new dispatch is made.  Economic participation factors for load below the sum of base points are calculated in the same way as the increasing ones.

EDC utilizes the Auto-Ranging Binary Search method.  It operates by dividing the search region into two, deciding which half the desired result is in, dividing that half into two, and so on until a solution is obtained.  Starting with the desired generation DESGEN (= sum of all generation from telemetry  +  FACE) and an initial value of LAMBDA (usually the value from the last EDC), the calculation proceeds until the error (MWn-DESGEN) is less than a set fraction of DESGEN.  This fraction, ERRTPW, resides in the database.

The binary search algorithm will always work for the Economic Dispatch Calculation when given a realistic set of conditions.  Discontinuous heat rate curve is also supported.  Discontinuous curves have slopes that are infinite at certain points.