## Description of Economic Dispatch

The Systems Lambda value reported is the indicated value occurring on each clock hour.  The value is calculated in the economic dispatch program.  Dayton Power and Light Company dispatches their units using standard Lagrangian techniques.  In other words, we attempt to operate our units at equal incremental cost where possible.  The value for system Lambda is given in $/MWH and represent the cost of the next MWH of power in our system available from generators being dispatched at that instant in time.  If no generators were being automatically dispatched on a particular clock hour, the system will keep System Lambda from the prior hour.

The actual “calculation” is performed via standard iterative methods.  Namely, the economic dispatch program estimates the value of System Lambda.  It then calculates the amount of generation needed at that time.  The value for System Lambda is then adjusted up or down until the amount of generation, as calculated from incremental cost curves for every generator, meets the current system requirements.

The incremental cost curves used by economic dispatch represent the cost of the next MWH available from a unit throughout its operating range.  The curves are a function of the unit’s heat rate efficiency, fuel cost, emission costs and variable maintenance cost.  As mentioned above, economic dispatch attempts to operate the generation at equal incremental costs.  That equal incremental cost value is termed System Lambda.