## Cover
FERC-714
Annual Electric Power System Report
Calendar Year 2004
From
Western Area Power Administration - Rocky Mountain Region
(WAPA-RMR)
A Power Marketing Administration under the authority of:
U.S. Dept. of Energy
Operator of NERC Control Area :
WAPA - Colorado Missouri (WACM)
This report covers
Transmission operated by WAPA-RMR
and
Power Plants Operated by the U.S. Bureau of Reclamation, Pick Sloan Western Division

## Pt I, Sch 1
Federal Energy Regulatory Commission |  | Annual Electric Control and Planning Area Report
FERC Form No. 714 (2004) |  | For the Year Ending December 31, 2004
Part I - Schedule 1. Identification and Certification
1. Respondent Identification: |  |  | 3. Respondent Mailing Address:
USDOE / WAPA - Rocky Mountain Region
attn: Operations Manager / J4000
Code: 28503 Name: WAPA - Rocky Mountain Region (WAPA-RMR) |  |  | P.O. Box 3700
Loveland, CO 80539-3700
2. Respondent Type: (Please check appropriate box and fill in name) |  |  | 4. Principal Contact Person:
Name: R. Paul Humberson
[ x ] Part I: Control Area (Complete Parts I, II, and IV)
Title: Manager, Transmission Scheduling and Security
Control Area Name: WAPA - Colorado Missouri (WACM) |  |  | Telephone: (970-461-7327)
[ x ] Part II: Planning Area (Complete Parts I, III, and IV) |  |  | 5. Certifying Official:
Name: Ed Hulls
Planning Area Name: WAPA-RMR, MEAN, RMGC, WMPA
Title: Operations Manager
Signature: ___________________ Date: ________
Return Completed Form to:
Federal Energy Regulatory Commission
Room 8B-06
888 First St. NE
Washington, D.C. 20426

## Pt II, Sch 1
Federal Energy Regulatory Commission |  | Annual Electric Control and Planning Area Report |  | Utility Code: 28503
FERC Form No. 714 (2004) |  | For the Year Ending December 31, 2004 |  | Utility Name: WAPA-RMR
Part II - Schedule 1.
|  | Generating Plants Included in Reporting Control Area |  | 7/13/2004 17:00:00 AM
Line No. | Electric Utility Name | Plant Name | Plant Available Capability at the Hour of the Annual Peak Demand Based on Net Energy for Load (MW) | Integrated Net Load on the Plant at the Hour of the Annual Peak Demand Based on Net Energy for Load (MW)
(a) | (b) | (c) | (d) | (e)
1 | WAPA / RMR / LAP | Alcova | 40 | 21
2 | WAPA / RMR / LAP | BigThompson | 5 | 3
3 | WAPA / RMR / LAP | Boysen | 6 | 6
4 | WAPA / RMR / LAP | BuffaloBill | 12 | 12
5 | WAPA / RMR / LAP | Estes | 34 | 3
6 | WAPA / RMR / LAP | Flatiron 1&2 | 86 | 25
7 | WAPA / RMR / LAP | Flatiron #3 | 0 | 0
8 | WAPA / RMR / LAP | FremontCanyon | 56 | 40
9 | WAPA / RMR / LAP | Glendo | 26 | 26
10 | WAPA / RMR / LAP | Green Mountain | 26 | 0
11 | WAPA / RMR / LAP | Guernsey | 8 | 0
12 | WAPA / RMR / LAP | Heart Mountain | 8 | 1
13 | WAPA / RMR / LAP | Kortes | 26 | 18
14 | WAPA / RMR / LAP | Mary's Lake | 0 | 0
15 | WAPA / RMR / LAP | Mount Elbert | 206 | 72
16 | WAPA / RMR / LAP | Pilot Butte | 2 | 2
17 | WAPA / RMR / LAP | Pole Hill | 35 | 10
18 | WAPA / RMR / LAP | Seminoe | 51 | 14
19 | WAPA / RMR / LAP | Shoshone | 4 | 3
20 | WAPA / RMR / LAP | Spirit Mountain | 3 | 3
21 | WAPA / RMR / LAP | Yellowtail | 186 | 47
22 | WAPA / RMR / CRSP | Towaoc | 11 | 5
23 | WAPA / RMR / CRSP | McPhee | 1 | 1
24 | Basin Electric Power Cooperative | Laramie River Station #2 | 550 | 550
25 | Basin Electric Power Cooperative | Laramie River Station #3 | 550 | 548
26 | Tri-State G&T | Craig #1 | 428 | 425
27 | Tri-State G&T | Craig #2 | 428 | 427
28 | Tri-State G&T | Craig #3 | 408 | 402
29 | Tri-State G&T | Nucla | 100 | 95
30 | Tri-State G&T | Williams Fork (DWB) | 3 | 0
31 | Tri-State G&T | Burlington | 100 | 0
32 | Tri-State G&T | Atlas | 82 | 63
33 | City of Colorado Springs, CO | ColoSprgs system | 1082 | 930
34 | Black Hills Power and Light | BlackHills system | 502 | 413
35 | Municipal Energy Ag'y of Nebraska | municipal Diesels | 23 | 5
39 |  | TOTAL | 5088 | 4170

## Pt II, Sch 2
Federal Energy Regulatory Commission |  | 39 | Annual Electric Control and Planning Area Report | [5 empty] | Utility Code: 28503
FERC Form No. 714 (2004) |  |  | For the Year Ending December 31, 2004 | [5 empty] | Utility Name:WAPA-RMR
Part II - Schedule 2. Control Area Monthly Capabilities at Time of Monthly Peak Demand
Net Capability at the Time of the Monthly Peak Demand, Based on Control Area Net Energy For Load (NEL) *
|  | Net Capability from Plants Reported on Schedule II |  |  |  |  | External to The Control Area
|  |  | Unavailable Capability Due to: |  |  |  | Net Unit or Firm Capability
|  | Available | Planned | Unplanned | Other | Total | (MW) |  | Total Capability
Line |  | Capability | Outage & Derating | Outage & Derating | Outage & Derating | (c + d + e + f) | Available * | Not Available | (g + h + i)
No. | Month | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW)
(a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
1 | Jan | 4002 | 283 | 480 | 0 | 4806 | 0 | 0 | 4806
2 | Feb | 4556 | 250 | 0 | 0 | 4806 | 0 | 0 | 4806
3 | Mar | 4556 | 123 | 212 | 0 | 4891 | 0 | 0 | 4891
4 | Apr | 3949 | 666 | 264 | 0 | 4879 | 0 | 0 | 4879
5 | May | 4590 | 627 | 133 | 0 | 5350 | 0 | 0 | 5350
6 | Jun | 5180 | 37 | 133 | 0 | 5350 | 0 | 0 | 5350
7 | Jul | 5088 | 209 | 53 | 0 | 5350 | 0 | 0 | 5350
8 | Aug | 5182 | 160 | 8 | 0 | 5350 | 0 | 0 | 5350
9 | Sep | 5187 | 116 | 47 | 0 | 5350 | 0 | 0 | 5350
10 | Oct | 4970 | 119 | 550 | 0 | 5401 | 0 | 0 | 5401
11 | Nov | 5156 | 168 | 77 | 0 | 5401 | 0 | 0 | 5401
12 | Dec | 5156 | 86 | 159 | 0 | 5401 | 0 | 0 | 5401

## Pt II, Sch 3
Federal Energy Regulatory Commission |  |  |  | Annual Electric Control and Planning Area Report | [5 empty] | Utility Code: 28503
FERC Form No. 714 (2004) |  |  |  | For the Year Ending December 31, 2004 | [5 empty] | Utility Name:WAPA-RMR
Part II - Schedule 3. Control Area Net Energy for Load and Peak Demand Sources by Month
Control Area Load Sources at Time of Control Area Monthly Peak Demand,
|  | Control Area | Net | Net Energy | Based on Net Energy For Load (NEL) *
|  | Net | Actual | for | Output of | Unit or Firm | Unit or Firm | Net Non-Firm | Monthly Peak | Monthly
Line |  | Generation | Interchange | Load (c - d) | Generating Plants | Purchases | Sales | & Inadvertent | Demand (f+g-h+i) | Minimum
No. | Month | (MWh) | (MWh) | (MWh) | (MW) | (MW) | (MW) | (MW) | (MW) | Demand (MW)
(a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
1 | Jan | 2729843 | 1029862 | 1699981 | 3830 | -197 | 846 | 20 | 2807 | 2385
2 | Feb | 2595913 | 1016931 | 1578982 | 4063 | -410 | 765 | -184 | 2704 | 2302
3 | Mar | 2389896 | 815313 | 1574583 | 3819 | -219 | 599 | -537 | 2464 | 2174
4 | Apr | 2127427 | 643008 | 1484419 | 2986 | -562 | 622 | 511 | 2313 | 1986
5 | May | 2170717 | 616409 | 1554308 | 3278 | -714 | 715 | 536 | 2385 | 1927
6 | Jun | 2509133 | 941243 | 1567890 | 3863 | -616 | 569 | 119 | 2797 | 2033
7 | Jul | 2721496 | 964204 | 1757292 | 4170 | -344 | 724 | -22 | 3080 | 2241
8 | Aug | 2647341 | 892318 | 1755023 | 3770 | -877 | 456 | 634 | 3071 | 1892
9 | Sep | 2370582 | 817218 | 1553364 | 4046 | -663 | 674 | 18 | 2727 | 2060
10 | Oct | 2322604 | 807511 | 1515093 | 3251 | -654 | 551 | 283 | 2329 | 1875
11 | Nov | 2407880 | 813864 | 1594016 | 3831 | -808 | 705 | 452 | 2770 | 2315
12 | Dec | 2607416 | 853348 | 1754068 | 4118 | -692 | 670 | 90 | 2846 | 2327
13 | Total | 29600248 | 10211229 | 19389019

## Pt II, Sch 4
Federal Energy Regulatory Commission |  | Annual Electric Control and Planning Area Report | Utility Code: 28503
FERC Form No. 714 (2004) |  | For the Year Ending December 31, 2004 | Utility Name:WAPA-RMR
Part II - Schedule 4. Adjacent Control Area Interconnections
Line No. | Name of Adjacent Control Area | Control Area Interconnection Line or Bus Names | Line or Bus Voltage (kV)
(a) | (b) | (c) | (d)
1 | WAUW | Yellowtail to Crossover | 230
2 | WAUE | David Hamill Converter Station (aka Stegall Dc tie, AC-DC-AC; asynchronous) | 230
3 | WAUE | Rapid City DC Tie | 230
4 | NPPD | Virginia Smith Converter Station (AC-DC-AC; asynchronous) | 230
5 | PNM | Waterflow to San Juan | 345
6 | WALC | Lost Canyon to Shiprock | 230
7 | WALC | Durango to Glade Tap | 115
8 | WALC | Morrow Point generation (dynamic) | 230
9 | WALC | Flaming Gorge generation (dynamic) | 138
10 | WALC | Blue Mesa generation (dynamic) | 115
11 | WALC | Crystal generation (dynamic) | 115
12 | PACE | Riverton | 230
13 | PACE | Wyodak to Buffalo | 230
14 | PACE | DJ 115 South | 115
15 | PACE | DJ 115 North | 115
16 | PACE | LRS to DJ | 230
17 | PACE | Antelope to DJ | 230
18 | PACE | Stegall to DJ | 230
19 | PACE | Casper -PACE | 115
20 | PACE | Casper - WAPA | 69
21 | PACE | Yellowtail | 230
22 | PACE | Thermopolis | 115
23 | PACE | Hilltop | 115
24 | PACE | Garland Canal generation (dynamic gen) | 12.5
25 | PACE | Sheridan Tap (dynamic load) | 230
26 | PACE | Badwater | 230
27 | PACE | Flaming Gorge to Rock Springs | 230
28 | PACE | Flaming Gorge to Bridger Valley | 69
29 | PACE | Vernal to Ashley | 138
30 | PACE | Vernal to Moon Lake | 138
31 | PACE | Vernal to Bonanza | 138
32 | PACE | Craig to Bonanza | 345
33 | PACE | Southwest Rangely to Artesia | 138
34 | PACE | Southwest Rangely to Meeker | 138
35 | PACE | Deserado Coal Mine | 13.8
36 | PSC | Mount Elbert to Malta | 230
37 | PSC | Weld 115 | 115
38 | PSC | Weld 230 | 230
39 | PSC | Ault to Fort St. Vrain | 230
40 | PSC | Fort St. Vrain to Longs Peak | 230
41 | PSC | Cobb Tap | 115
42 | PSC | Rawhide generation (dynamic) | 230
43 | PSC | Rawhide CT(dynamic) | 24/230
44 | PSC | PRPA load (dynamic) | multiple 13.8
45 | PSC | Monument to Daniels Park | 115
46 | PSC | Gore Tap transformer | 230
47 | PSC | Ponnequin | 115
48 | PSC | Forest Lake | 115
49 | PSC | Fuller | 115
50 | PSC | Beaver Creek | 115
51 | PSC | Story | 230
52 | PSC | Peetz | 115
53 | PSC | Cheyenne Light Fuel & Power (dynamic) | 115
54 | PSC | Midway | 230
55 | PSC | Canon West | 230
56 | PSC | Salida | 115
57 | PSC | Rifle | 230 & 115
58 | PSC | Grand Junction | 230 & 115
59 | PSC | Poncha to San Luis Valley | 230
60 | PSC | Hayden | 230 & 138
61 | PSC | Craig transfer (dynamic load) | 230
62 | PSC | Mill to Fraser | 115
63 | PSC | Rifle(Atlas) generation (dynamic) | 230
64 | PSC | Limon | 13.8/230

## Pt II, Sch 5
Federal Energy Regulatory Commission |  | Annual Electric Control and Planning Area Report |  |  |  | Utility Code: 28503
FERC Form No. 714 (2004) |  | For the Year Ending December 31, 2004 |  |  |  | Utility Name:WAPA-RMR
Part II - Schedule 5.
Control Area Scheduled and Actual Interchange
|  |  | Scheduled Interchange |  | Actual Interchange Between
Line | Name of Control Area |  | Between Control Areas |  | Adjacent Control Areas
No. |  |  | (MWH) |  | (MWH)
|  |  | Received (-) | Delivered (+) | Received (-) | Delivered (+)
(a) | (b) |  | (c) | (d) | (e) | (f)
1 | WAPA - Upper Great Plains East (WAUE) |  | -631020 | 0 | -631020 | 0
2 | Public Service Co of Colorado (PSCO) |  | 0 | 8498239 |  | 8452948
3 | PacifiCorp - East (PACE) |  |  | 1372391 |  | 2470042
4 | WAPA - Upper Great Plains West (WAUW) |  | -98156 |  | -715758
5 | Nebraska Public Power District (NPPD) |  | -764151 | 0 | -764151 | 0
6 | WAPA - Lower Colorado (WALC) |  |  | 931643 |  | 123561
7 | Public Service of New Mexico (PNM) |  |  | 902283 | 0 | 1281293
8
9
10 |  | TOTAL | -1493327 | 11704556 | -2110929 | 12327844

## Pt II, Sch 6
Federal Energy Regulatory Commission | Annual Electric Control and Planning Area Report | Utility Code: 28503
FERC Form No. 714 (2004) | For the Year Ending December 31, 2004 | Utility Name:WAPA-RMR
Part II - Schedule 6. Control Area System Lambda
The WACM control area does not record system Lambda data. There are nine (9) different Load
Serving Entities (LSE) within the WACM control area and two Federal preference power marketing plans. The Area
Control Error (ACE) for WACM is responded to entirely by the LAP units of WAPA-RMR and 20 MW of CRSP which
are hydro-electric generation only. WAPA-RMR has no ownership of or rights to any thermal
resources. Therefore, there is no lambda signal developed, recorded, or used in the operation of the
WACM control area. The LSE's have different resource mixes that include mostly thermal
generation. Most of the LSE's have their own minimal cost operating algorithm used for economic dispatch of
their own resources. These algorithms generally include some market mechanism for replacing native
resources when market prices are less. Thus, economic dispatch is generally the common goal, but at the LSE level,
rather than the control area level.

## Pt III, Sch 1
Federal Energy Regulatory Commission |  | Annual Electric Control and Planning Area Report |  | Utility Code: 28503
FERC Form No. 714 (2004) |  | For the Year Ending December 31, 2004 |  | Utility Name:WAPA-RMR
Part III - Schedule 1. Electric Utilities That Compose the Planning Area
Electric Utility Coincident
Line | Electric Utility Name |  | Peak Demand (MW)
No. |  |  | Summer * | Winter *
(a) | (b) |  | (c) | (d)
1 | Municipal Energy Agency of Nebraska (MEAN) |  | 113.5 | 95.1
2 | Wyoming Municipal Power Agency (WMPA) |  | 42 | 39
3 | Rocky Mountain Generation Cooperative (RMGC) |  | 8 | 7
4 | WAPA - RMR all requirements loads & losses on firm contracts |  | 62.5 | 56.2
5
6 |  | TOTAL | 226 | 197.3
7
8
9
10
11

## Pt III, Sch 2
Federal Energy Regulatory Commission | Annual Electric Control and Planning Area Report | Utility Code: 28503
FERC Form No. 714 (2004) | For the Year Ending December 31, 2004 | Utility Name:WAPA-RMR
Part III - Schedule 2.
Planning Area Hourly Demand Forecast Summer and Winter Peak Demand and Annual Net Energy for Load
The following electronic files have been prepared and submitted on Western's behalf by WSCC 1. Hourly WACM Control Area Load for the period Jan 1, 2004 - Dec 31, 2004. * The following electronic files have been prepared and are attached. 2. WAPA planning area's forecast summer and winter peak demand, and annual net energy for load, for the next 10 years. * A printout of this data has been inserted after this page.

## Pt III, Sch2,Fcast
1.77% | Planning Area forecast for WAPA-RMR
Attached to 2004 FERC 714 Part 3, Schedule 2 for utility 28503
| TOTAL | TOTAL | TOTAL |  | WAPA-RMR
| MW | MW | GWh |  | MW | MW | GWh
| SUMMER | WINTER |  |  | SUMMER | WINTER
2004 | 226 | 208.2 | 1119 | 2004 | 62.5 | 56.2 | 212
2005 | 228.7524 | 210.7665 | 1134.222 | 2005 | 62.5 | 56.2 | 212
2006 | 231.5534 | 213.3784 | 1149.7134 | 2006 | 62.5 | 56.2 | 212
2007 | 234.4041 | 216.0366 | 1165.4791 | 2007 | 62.5 | 56.2 | 212
2008 | 237.3052 | 218.7418 | 1181.5237 | 2008 | 62.5 | 56.2 | 212
2009 | 240.2576 | 221.4949 | 1197.8524 | 2009 | 62.5 | 56.2 | 212
2010 | 243.2623 | 224.2967 | 1214.4701 | 2010 | 62.5 | 56.2 | 212
2011 | 246.3202 | 227.1481 | 1231.3819 | 2011 | 62.5 | 56.2 | 212
2012 | 249.4322 | 230.05 | 1248.5931 | 2012 | 62.5 | 56.2 | 212
2013 | 252.5993 | 233.0032 | 1266.1089 | 2013 | 62.5 | 56.2 | 212
| MEAN | MEAN | MEAN |  | WMPA | WMPA | WMPA
| MW | MW | GWh |  | MW | MW | GWh
| SUMMER | WINTER |  |  | SUMMER | WINTER
2004 | 113.5 | 106 | 615 | 2004 | 42 | 39 | 245
2005 | 115.5089 | 107.8762 | 625.8855 | 2005 | 42.7434 | 39.6903 | 249.3365
2006 | 117.5535 | 109.7856 | 636.9637 | 2006 | 43.5 | 40.3928 | 253.7498
2007 | 119.6342 | 111.7288 | 648.2379 | 2007 | 44.2699 | 41.1078 | 258.2411
2008 | 121.7517 | 113.7064 | 659.7117 | 2008 | 45.0535 | 41.8354 | 262.812
2009 | 123.9067 | 115.719 | 671.3886 | 2009 | 45.8509 | 42.5759 | 267.4638
2010 | 126.0998 | 117.7672 | 683.2722 | 2010 | 46.6625 | 43.3295 | 272.1979
2011 | 128.3318 | 119.8517 | 695.3661 | 2011 | 47.4884 | 44.0964 | 277.0158
2012 | 130.6033 | 121.9731 | 707.6741 | 2012 | 48.329 | 44.8769 | 281.919
2013 | 132.9149 | 124.132 | 720.1999 | 2013 | 49.1844 | 45.6712 | 286.9089
| RMGC | RMGC | RMGC
| MW | MW | GWh | NOTE: diskettes have been submitted
| SUMMER | WINTER |  | per requirements.
2004 | 8 | 7 | 47
2005 | 8 | 7 | 47
2006 | 8 | 7 | 47
2007 | 8 | 7 | 47
2008 | 8 | 7 | 47
2009 | 8 | 7 | 47
2010 | 8 | 7 | 47
2011 | 8 | 7 | 47
2012 | 8 | 7 | 47
2013 | 8 | 7 | 47

## Pt IV
Federal Energy Regulatory Commission |  |  |  | Annual Electric Control and Planning Area Report |  | Utility Code: 28503
FERC Form No. 714 (2003) |  |  |  | For the Year Ending December 31, 2003 |  | Utility Name:WAPA
Part IV. Notes
Page | Line
No. | No. | Column |  |  | Notes
(a) | (b) | (c) |  |  | (d)
11 | all | c,d,e,f | net actual interchange and net schedule coordinated with reconciled monthly NERC inadvertant accountings, not individual utilities
11 | all but 6 | c,d,e,f | only net metering and net schedule totals are available in EMS archives
12 |  |  | WACM does not use thermal for control, therefore no lambda is recorded. See required description on page 12 (Pt 2, Schd 6)
13 | all | all | LSE's with load in WACM reporting Part III, Schd2, #2 forecast data separately should include : BEPC, TSGT, BHPL, PSCO, PACIFICORP, COLORADO SPRINGS